## Documents
Slug | Name | Short Code | Sections | Requirements | Created
architecture-decisions | Architecture Decisions | ARC | 1 | 8 | 2026-03-26T00:34:31.149Z
interface-requirements | Interface Requirements | IFC | 1 | 28 | 2026-03-26T00:34:30.865Z
stakeholder-requirements | Stakeholder Requirements | STK | 1 | 18 | 2026-03-26T00:34:30.333Z
subsystem-requirements | Subsystem Requirements | SUB | 1 | 61 | 2026-03-26T00:34:31.009Z
system-requirements | System Requirements | SYS | 1 | 15 | 2026-03-26T00:34:30.727Z
verification-requirements | Verification Requirements | VER | 1 | 59 | 2026-03-26T00:34:31.300Z

## Requirements
Ref | Text | Document | Section | Pattern | Verification | QA Score | Compliance | Rationale | Tags
ARC-REQ-001 | The Emergency Diesel Generator design SHALL employ a medium-speed 4-stroke turbocharged diesel engine operating at 750 rpm or 1,000 rpm, achieving a start-on-demand probability of not less than 0.975. | architecture-decisions | Architecture Decisions |  | Inspection | 100 |  | Medium-speed 4-stroke turbocharged diesels (750/1000 rpm) are the established nuclear-grade choice for emergency power: they achieve >0.975 start-on-demand probability, are qualified under IEEE 387 and IEC 60034 by multiple OEMs, and have 5,000+ hour overhaul intervals compatible with refuelling outage maintenance cycles. High-speed units achieve faster start but exhibit inferior long-term reliability; 2-stroke diesels are not available at the required power class. | architecture, engine, session-570, idempotency:arc-engine-570, informational, session-572, reqs-eng-session-577
ARC-REQ-002 | The Emergency Diesel Generator design SHALL implement engine protection trip functions (overspeed, overtemperature, low oil pressure) as hardwired relay circuits physically independent of the digital monitoring and control system. | architecture-decisions | Architecture Decisions |  | Inspection | 100 |  | Separation of protection and control is mandated by IEC 61513 (Nuclear power plants — I&C systems — General requirements for systems) and UK ONR Safety Assessment Principles (SAPs). Hardwired relay protection provides deterministic, software-independent trip response and eliminates common-cause software failure and cyber vulnerabilities (hazard H-010) from the safety-critical trip path. | architecture, ic-system, session-570, idempotency:arc-ic-separation-570, informational, session-572, reqs-eng-session-577
ARC-REQ-003 | The Emergency Diesel Generator design SHALL provide two fully independent trains (Train A and Train B), each with dedicated engine, generator, fuel storage, cooling, starting air, I&C, and switchgear housed in separate fire-rated buildings. | architecture-decisions | Architecture Decisions |  | Inspection | 100 |  | Train independence is required by UK GDA process and ONR SAPs to meet single-failure criterion: any active failure in one train must not prevent the other train from fulfilling its safety function. Physical separation in fire-rated buildings eliminates propagating hazards (fire, flood) and directly supports the N+1 redundancy allocation across EDG trains A and B. | architecture, redundancy, session-570, idempotency:arc-train-independence-570, informational, session-572, reqs-eng-session-577
ARC-REQ-004 | The Emergency Diesel Generator design SHALL use compressed-air starting with air receivers sized for not fewer than 5 consecutive start attempts without recharge. | architecture-decisions | Architecture Decisions |  | Demonstration | 100 |  | Compressed air starting is the industry standard for diesel engines above 500 kW. It provides consistent cranking torque (15-25 bar) independent of ambient temperature, whereas battery cold-cranking capacity degrades by ~40% below 0°C. Five consecutive starts per demand event are consistent with IEEE 387 starting-reliability requirements. | architecture, starting-air, session-570, idempotency:arc-starting-570, informational, session-572, reqs-eng-session-577
ARC-REQ-005 | The Emergency Diesel Generator design SHALL integrate LOOP detection, generator breaker control, and load sequencing within a single Electrical Switchgear and Load Sequencer subsystem sharing the 6.6 kV bus environment. | architecture-decisions | Architecture Decisions |  | Inspection | 100 |  | Grouping these functions in one subsystem reduces the interface count and eliminates race conditions from distribution across I&C and power subsystems. All three functions share the 6.6 kV bus environment, common failure modes, and are tested together under IEEE 387 load-acceptance tests. A single subsystem boundary simplifies post-event audit trails for nuclear post-event analysis. | architecture, switchgear, session-570, idempotency:arc-switchgear-570, informational, session-572, reqs-eng-session-577
ARC-REQ-006 | The Emergency Diesel Generator design SHALL implement engine cooling as a dedicated subsystem independent of the Diesel Engine Assembly, with a separate fault tree analysis satisfying SIL 2 targets for hazard H-006. | architecture-decisions | Architecture Decisions |  | Inspection | 100 |  | Hazard H-006 (cooling system failure) is classified SIL 2 under IEC 61508 (Functional safety of E/E/PE safety-related systems), requiring independent fault tree analysis. The cooling subsystem has distinct failure modes (fan belt, radiator blockage, coolant chemistry degradation) not correlated with engine mechanical failure, interfaces externally to a separate heat sink, and requires a distinct maintenance regime. | architecture, cooling, session-570, idempotency:arc-cooling-570, informational, session-572, reqs-eng-session-577
ARC-REQ-007 | ARC: EDG Building and Support Systems — Seismic Category I dedicated enclosure with four integrated sub-functions. The building is decomposed into: (1) EDG Building Structure (Seismic Cat I reinforced concrete providing missile/blast protection and inter-train physical separation); (2) EDG Building HVAC System (Class 1E ventilation providing combustion air and room cooling, auto-starting with engine); (3) EDG Flood and Drainage System (passive barriers plus active bunded sump providing worst-case flood containment without affecting engine operability); (4) EDG Building Access Control System (security zone management, SIL 0, backed by Class 1E 125VDC). Alternatives considered: (a) shared HVAC between trains — rejected because common-cause HVAC failure could disable both trains; (b) active flood pumps as primary barrier — rejected because passive first-line protection is more reliable during LOOP when pump power may be interrupted. The SIL 2 allocation applies to Structure, HVAC, and Flood systems; Access Control is SIL 0 (security function, not safety). | architecture-decisions | Architecture Decisions |  | Inspection |  |  | Decomposition decision required to prevent common-cause structural, thermal, and flood failure paths from coupling the two EDG trains. Each component has distinct failure modes and testing intervals, necessitating separate classification and independent requirement derivation. SIL 2 is inherited from SYS-REQ-009 (seismic) and SYS-REQ-011 (fire/flood) which bound the building safety functions. | architecture, edg-building, session-586, idempotency:arc-edg-building-586, informational, qc-session-589
ARC-REQ-008 | ARC: Fuel Oil System — Gravity-fed Day Tank with automatic transfer from bulk storage. The system uses a two-level storage architecture (Bulk Storage Tank → Day Tank → engine) to decouple the engine from the bulk transfer system. The Day Tank is elevated to provide gravity-fed fuel supply to the injection pump without a booster pump, eliminating a potential single-point failure in the fuel supply path. Fuel transfer is controlled by float-switch automation rather than a timed sequence to accommodate variable engine fuel consumption rates across the load range. The Bulk Storage Tank is sized at 110% of the 7-day SYS requirement to provide operating margin for the gravity-feed architecture's inability to fully drain to zero. | architecture-decisions | Architecture Decisions |  | Inspection |  |  | The two-level gravity-feed architecture was selected over a direct single-tank pumped supply because: (1) Day Tank gravity feed eliminates pump failure as an engine starvation cause; (2) the architectural separation allows the bulk transfer pump to be maintained or replaced without interrupting engine operation; (3) float-switch control is simpler and more reliable than timed or flow-metered control in a nuclear qualified environment. | architecture, fuel-oil, session-591, idempotency:arc-fuel-oil-system-591
IFC-REQ-001 | The interface between the Emergency Diesel Generator and the National Grid SHALL detect loss of offsite power via redundant undervoltage relays monitoring 6.6kV bus voltage, with relay pickup at 90% nominal (5.94kV) and dropout at 70% nominal (4.62kV), and a time delay of no more than 100ms to discriminate between LOOP and transient voltage dips. | interface-requirements | Interface Requirements |  | Test | 86 |  | External interface with National Grid. MoP basis: 90% nominal (5.94 kV) relay pickup is the IEEE C37.90 (Relays and Relay Systems Associated with Electric Power Apparatus) minimum undervoltage threshold for safety bus protection, confirmed as the ONR-preferred discrimination point between LOOP and motor starting voltage dips (typically 85-90% nominal). 70% dropout (4.62 kV) provides hysteresis to prevent relay chatter during voltage recovery. The 100 ms discrimination delay is derived from the maximum duration of a motor-starting voltage dip on the 6.6 kV bus; false positives consume reliability margin and trigger unnecessary maintenance entries. | interface, external, session-570, idempotency:ifc-ext-grid-570, reqs-eng-session-577
IFC-REQ-002 | The interface between the Emergency Diesel Generator and the Emergency AC Bus SHALL deliver 6.6kV 3-phase 50Hz power through a generator output breaker rated for the full fault current of the bus, with the generator breaker closing within 500ms of the EDG reaching rated voltage and frequency. | interface-requirements | Interface Requirements |  | Test | 86 |  | External interface with Emergency AC Bus: the generator breaker is the boundary between EDG output and plant safety loads. Breaker closing time directly adds to the total power restoration time. | interface, external, session-570, idempotency:ifc-ext-bus-570
IFC-REQ-003 | The interface between the Emergency Diesel Generator and the Ultimate Heat Sink SHALL provide cooling water flow of at least 150 m3/h at a maximum inlet temperature of 30°C for engine jacket water and aftercooler heat rejection, when a water-cooled design is selected. | interface-requirements | Interface Requirements |  | Test | 86 |  | External interface with Ultimate Heat Sink. MoP basis: 150 m3/h cooling water flow rate is derived from the engine OEM thermal balance calculation: at rated brake power, jacket water heat rejection is approximately 1.2 MW requiring this flow at a 5°C temperature rise across the heat exchanger. The 30°C maximum inlet temperature is the UK coastal site 99th percentile sea/river water temperature from UK Met Office climatological data; exceeding this would reduce heat exchanger effectiveness and drive coolant temperature above the 88°C jacket water thermostat setpoint under sustained full-load operation. | interface, external, session-570, idempotency:ifc-ext-uhs-570, reqs-eng-session-577
IFC-REQ-004 | The interface between the Emergency Diesel Generator and the Plant Protection System SHALL accept a hardwired LOOP start signal (24VDC energise-to-start) and provide EDG status feedback signals (running, loaded, tripped, available) to the protection system safeguards logic. | interface-requirements | Interface Requirements |  | Test | 86 |  | External interface with Plant Protection System: the start signal is the safety-critical command that initiates EDG response. Hardwired implementation per IEC 61513 (Nuclear power plants — Instrumentation and control important to safety) ensures independence from digital system common cause failure. | interface, external, session-570, idempotency:ifc-ext-pps-570
IFC-REQ-005 | The interface between the Emergency Diesel Generator and the Main Control Room SHALL provide continuous analogue and digital signals for display of EDG operating parameters, alarm inputs for all abnormal conditions, and command outputs for manual start/stop and transfer authorisation, over qualified Class 1E cabling. | interface-requirements | Interface Requirements |  | Demonstration | 86 |  | External interface with Main Control Room: operator situational awareness depends on real-time parameter display. All scenarios require operator monitoring and command capability from MCR. | interface, external, session-570, idempotency:ifc-ext-mcr-570
IFC-REQ-006 | The interface between the Emergency Diesel Generator and the Fuel Supply infrastructure SHALL accept diesel fuel delivery via road tanker to bulk storage tanks through a fill connection with overfill protection, with automatic day tank level management maintaining a minimum 2-hour fuel reserve at all times. | interface-requirements | Interface Requirements |  | Inspection | 86 |  | External interface with Fuel Supply: the fill connection and overfill protection are the boundary between off-site logistics and on-site fuel management. The 2-hour day tank reserve ensures EDG continues running even if bulk transfer pump fails temporarily. | interface, external, session-570, idempotency:ifc-ext-fuel-570
IFC-REQ-007 | The interface between the Emergency Diesel Generator and the DC Battery System SHALL provide 125VDC Class 1E control power for EDG instrumentation and control, and 24VDC starting battery power for air start solenoid valves, with battery chargers powered from the EDG output bus to maintain charge during LOOP. | interface-requirements | Interface Requirements |  | Test | 86 |  | External interface with DC Battery System: DC power is essential for EDG control and starting. The battery charger feedback loop (EDG powers charger, charger maintains battery, battery enables next start) must be validated for extended LOOP scenarios. | interface, external, session-570, idempotency:ifc-ext-dc-570
IFC-REQ-008 | The interface between the Diesel Engine Assembly (Fuel Injection System) and the Fuel Oil System SHALL deliver filtered diesel fuel at 3.0 to 5.0 bar gauge feed pressure at the injection pump inlet, with fuel cleanliness compliant with ISO 4406 cleanliness class 18/16/13, and a minimum flow rate of 1.5× maximum injection pump demand at rated power. | interface-requirements | Interface Requirements |  | Test | 86 |  | The injection pump requires minimum feed pressure to prevent vapour locking and maintain injection accuracy; 3.0 bar provides a positive pressure margin above injection pump inlet requirements even at maximum ambient temperature. ISO 4406 cleanliness class 18/16/13 is consistent with the injection pump manufacturer's requirement for particulate cleanliness; contamination above this level causes accelerated pump barrel-plunger wear. The 1.5× flow factor accounts for fuel return flow from the overflow valve and provides margin during transient load demand. | interface, diesel-engine-assembly, sil-3, session-571, idempotency:ifc-dea-fuel-supply-571
IFC-REQ-009 | The interface between the Diesel Engine Assembly (Engine Block) and the Engine Cooling System SHALL accept coolant flow at the engine inlet at a minimum of 120 m3/h at 70°C to 85°C inlet temperature, with jacket water pressure at the engine block coolant ports maintained between 0.5 and 2.0 bar gauge to prevent cavitation erosion of the wet-liner cylinder bores. | interface-requirements | Interface Requirements |  | Test | 86 |  | Jacket water temperature range and flow rate are set by the engine OEM thermal model to keep metal temperatures within allowable limits: cylinder liner temperature must remain below 180°C to prevent lubricant film breakdown; below 70°C inlet temperature causes condensation and acid corrosion in the liner bores. Jacket water pressure must be positive to prevent cavitation erosion of aluminium-bronze liners during high-frequency combustion pressure pulses — a known failure mode in medium-speed diesels operating below minimum specified flow. Interface defined here because the cooling system is a separate SIL-2 subsystem per ARC-REQ-006. | interface, diesel-engine-assembly, sil-3, session-571, idempotency:ifc-dea-cooling-571
IFC-REQ-010 | The interface between the Diesel Engine Assembly (Engine Block, Turbocharger) and the Lubrication Oil System SHALL provide lubricating oil at the main gallery entry at 4.0 to 6.5 bar gauge and oil temperature between 60°C and 90°C, with oil cleanliness compliant with ISO 4406 class 16/14/11, sustained from cold start until the engine reaches rated speed. | interface-requirements | Interface Requirements |  | Test | 86 |  | Main gallery oil pressure of 4.0-6.5 bar is the OEM requirement for hydrodynamic bearing film formation at 750 rpm; the low-pressure trip at 2.0 bar (SUB-REQ-005) provides a 2 bar margin below minimum operating pressure. Oil temperature below 60°C causes high viscosity and reduced flow to the turbocharger bearings, risking coking during start-up; above 90°C the oil viscosity drops below the minimum for bearing film formation. The ISO 4406 cleanliness class is tighter than the fuel requirement because the turbocharger bearings at 30,000+ rpm are more sensitive to particulate contamination than the injection pump. | interface, diesel-engine-assembly, sil-3, session-571, idempotency:ifc-dea-lubrication-571
IFC-REQ-011 | The Starting Air System–Engine Assembly interface SHALL supply 25–30 bar compressed air to the air start distributor inlet, cranking the engine to at least 120 rpm within 1.5 seconds of start signal at -10°C ambient. | interface-requirements | Interface Requirements |  | Test | 71 |  | Air start distributor inlet pressure of 25-30 bar is the OEM cranking design pressure, providing enough torque to overcome cold-oil viscosity at -10°C ambient; below 20 bar the cranking torque is insufficient for reliable self-sustaining combustion achievement within the 3-second budget (SUB-REQ-001). The 120 rpm minimum cranking speed is the threshold at which compression-ignition diesels reliably achieve first combustion on qualified nuclear-grade engines. Per ARC-REQ-004, the compressed air starting choice is driven by consistent cold-weather cranking torque versus battery starting alternatives. | interface, diesel-engine-assembly, sil-3, session-571, idempotency:ifc-dea-starting-air-571, reqs-eng-session-583
IFC-REQ-012 | The interface between the Diesel Engine Assembly and the EDG Instrumentation and Control System SHALL provide continuous 4-20 mA analogue signals for: engine speed (0-1000 rpm), jacket water outlet temperature (0-120°C), lubricating oil pressure (0-10 bar), and fuel rack position (0-100%); and SHALL provide hardwired 24VDC discrete inputs from the Engine Protection Relay Package to the I&C for each trip function status (overspeed, high coolant temp, low oil pressure, overcurrent), with signal cable rated for Class 1E nuclear service per IEEE Std 383 (Standard for Type Testing of Class 1E Electric Cables, Field Splices, and Connections for Nuclear Power Generating Stations). | interface-requirements | Interface Requirements |  | Inspection | 86 |  | The 4-20 mA standard loop signal is the nuclear industry standard for qualified analogue instrumentation — it is immune to common mode voltage, allows wire-break detection (open = 0 mA), and is compatible with Class 1E qualified transmitters and I&C input cards. The parameter ranges are set to span the full operating and alarm ranges with 10% headroom. The hardwired discrete inputs for protection status ensure the I&C system receives protection status via a deterministic path, not via network communication which could be disrupted. Class 1E cable qualification per IEEE Std 383 is required for safety system cabling in nuclear plants. | interface, diesel-engine-assembly, sil-3, session-571, idempotency:ifc-dea-ic-signals-571
IFC-REQ-013 | The interface between the Diesel Engine Assembly (Crankshaft and Flexible Shaft Coupling) and the Synchronous Generator rotor shaft SHALL transmit rated mechanical power at 750 rpm with maximum torsional vibration amplitude not exceeding ±5% of rated torque at any harmonic order, and SHALL accommodate misalignment of up to 0.3 mm parallel offset and 0.1° angular without transmitting bending loads to either crankshaft or generator shaft bearing. | interface-requirements | Interface Requirements |  | Test | 86 |  | The torsional vibration limit of ±5% is derived from the synchronous generator's design basis for oscillatory torque on the rotor shaft and drive-end bearing — exceeding this causes cyclic fatigue in the shaft key and coupling hub. The misalignment tolerance of 0.3 mm / 0.1° is the flexible coupling manufacturer's specification for the expected thermal growth differential between the engine and generator frames under operating conditions; rigidly coupling without misalignment accommodation would transmit bending moments to the crankshaft main bearings, violating their design load case. | interface, diesel-engine-assembly, sil-3, session-571, idempotency:ifc-dea-generator-coupling-571
IFC-REQ-014 | The interface between the EDG Instrumentation and Control System and the Starting Air System Air Start Valve SHALL transmit a 125VDC Class 1E start command via a dedicated hardwired discrete signal, energising the solenoid valve within 200 ms of LOOP detection to initiate engine cranking. | interface-requirements | Interface Requirements |  | Test | 86 |  | The start command interface is on the critical timing path between LOOP detection and engine cranking. A hardwired discrete signal (not networked) is required to achieve the deterministic 200 ms timing budget and to maintain SIL 3 integrity — network-routed commands introduce non-deterministic latency and shared-cause vulnerability. 125VDC Class 1E power ensures the interface remains functional under loss of normal AC power, which is the exact condition requiring EDG start. | interface, starting-air-system, ic-system, sil-3, session-581, idempotency:ifc-ic-sas-start-command-581
IFC-REQ-015 | The interface between the Starting Air System Pressure Monitoring and Low-Pressure Alarm and the EDG Instrumentation and Control System SHALL transmit continuous 4-20 mA analogue pressure signals from each receiver bank at a minimum scan rate of 1 Hz, with hardwired discrete alarm contacts closing within 5 seconds of low-pressure threshold being reached. | interface-requirements | Interface Requirements |  | Test | 86 |  | Continuous pressure monitoring enables trend-based maintenance scheduling and early detection of receiver leakage. The 1 Hz scan rate is sufficient to track pressure decay curves between start attempts. The hardwired alarm contact is required independently of the analogue signal so that the alarm function is not defeated by I&C software failure — consistent with SIL 3 architecture requiring independence of alarm and control paths. | interface, starting-air-system, ic-system, session-581, idempotency:ifc-sas-pressure-to-ic-581
IFC-REQ-016 | The interface between the Bus Undervoltage Sensing Relay and the Generator Circuit Breaker shall carry a hardwired Class 1E 125VDC discrete start initiation signal; the signal shall be current-limited to 50mA, the cable routing shall be segregated from non-Class 1E cabling per IEEE 384, and signal transmission shall be failsafe such that an open-circuit condition is interpreted as a start demand. | interface-requirements | Interface Requirements |  | Test | 86 |  | Hardwired 125VDC discrete interface prevents cyber interference with the LOOP initiation path per SYS-REQ-012. 50mA current limit prevents cable insulation damage from a ground fault causing an inadvertent start. IEEE 384 segregation ensures a fire or cable fault cannot simultaneously disable both the signal and the return circuit. Open-circuit failsafe ensures cable damage generates a conservative start demand rather than silently defeating the safety function. | interface, electrical-switchgear-and-load-sequencer, sil-3, safety-critical, session-582, idempotency:ifc-buvr-gcb-start-582
IFC-REQ-017 | The interface between the Synchronising Check Relay and the Generator Circuit Breaker SHALL carry a hardwired 125VDC discrete close-permission signal active only when synchronising conditions are satisfied or dead-bus override is active; the interface SHALL include a mechanical anti-pumping interlock preventing more than one close attempt per close command, and the permissive signal SHALL be removed within 50ms of a synchronising condition violation. | interface-requirements | Interface Requirements |  | Test | 86 |  | Hardwired close permission keeps the synchronising function independent of digital control systems. Anti-pumping interlock prevents repeated GCB close-open-close cycles on a marginal synchronising condition, which would mechanically stress the GCB mechanism and risk weld failure of contacts. 50ms permissive withdrawal time ensures the GCB cannot complete a close operation outside the synchronising window given its 100ms mechanical close time, preventing out-of-phase closure. | interface, electrical-switchgear-and-load-sequencer, sil-3, session-582, idempotency:ifc-scr-gcb-close-permission-582
IFC-REQ-018 | The interface between the Generator Electrical Protection Relay Package and the Generator Circuit Breaker SHALL deliver a hardwired trip signal via a dedicated Class 1E trip coil circuit with a maximum resistance of 10 ohms total (cable plus coil), the trip contact shall be rated for interrupting 5A inductive DC load at 125VDC, and the trip circuit shall be continuously supervised such that a broken or high-resistance circuit triggers an alarm to the Main Control Room within 5 seconds. | interface-requirements | Interface Requirements |  | Test | 86 |  | Maximum 10 ohm trip circuit resistance ensures the GCB trip coil receives minimum 11.9A at lowest battery voltage (95VDC), exceeding the minimum trip coil pick-up current. Trip contact 5A inductive DC rating matches the GCB trip coil inrush current at 125VDC. Continuous trip circuit supervision (wiring integrity monitoring) detects broken trip wires before a protection demand occurs; the 5-second alarm delay filters transient monitoring glitches without leaving the generator unprotected. Required per BS EN 60947-2 circuit breaker protection application. | interface, electrical-switchgear-and-load-sequencer, sil-3, safety-critical, session-582, idempotency:ifc-geprp-gcb-trip-582
IFC-REQ-019 | The interface between the Ventilation and Combustion Air System and the Diesel Engine Assembly SHALL supply combustion air at a velocity not exceeding 8 m/s at the engine air intake plenum, with particulate filtration to ISO 16890 ePM1 55% efficiency to prevent ingestion of construction debris or environmental particulates. | interface-requirements | Interface Requirements |  | Test |  |  | Excessive inlet velocity causes turbulent losses in the engine air intake, degrading volumetric efficiency and potentially raising intake manifold temperature. The 8 m/s limit matches engine OEM intake ductwork design constraints. ISO 16890 ePM1 55% filtration is the minimum grade that prevents turbocharger fouling during the expected 7-day extended run period per nuclear ConOps. | interface, edg-building, hvac, session-586, idempotency:ifc-hvac-engine-air-586
IFC-REQ-020 | The interface between the Fire Detection and Suppression System and the Ventilation and Combustion Air System SHALL transmit a hardwired ventilation isolation signal within 5 seconds of confirmed fire detection, causing the Ventilation and Combustion Air System to close all dampers and shut off fans to prevent gaseous suppression agent dilution. | interface-requirements | Interface Requirements |  | Test |  |  | Gaseous total-flood fire suppression (CO2 or FM200) requires isolation of all air paths into the protected enclosure to maintain agent concentration above the minimum extinguishing design concentration for 10 minutes per NFPA 2001 and BS EN 15004. If ventilation continues, the agent disperses below minimum concentration before the fire is extinguished. The 5-second isolation time precedes typical suppression discharge delay of 30-60 seconds, ensuring ventilation is off before agent release. | interface, edg-building, fire, hvac, session-586, idempotency:ifc-fire-hvac-shutdown-586
IFC-REQ-021 | The interface between the Drain and Spill Containment System and the Fuel Oil System SHALL provide a continuous bunded collection path for all Fuel Oil System components within the EDG building, such that any fuel release up to the full day-tank volume (4,000 litres) is captured within the sump without reaching an ignition source or drainage to uncontrolled discharge. | interface-requirements | Interface Requirements |  | Inspection |  |  | The Fuel Oil System day tank is the largest single flammable fluid inventory in the EDG building. Without a continuous bunded path from every fuel connection to the sump, a pipe joint failure or tank overflow would flow across an unprotected floor to the engine exhaust system, which operates at 600-700°C and provides an ignition source. This interface requirement enforces the physical routing of drains established by the fire risk assessment per UK HSE Process Safety Management standards. | interface, edg-building, flood, fuel, session-586, idempotency:ifc-drain-fuel-contain-586
IFC-REQ-022 | The interface between the Coolant Circulation Pump and the Engine Jacket Water Circuit SHALL transmit coolant at a minimum flow rate of 150 L/min at 0.8 bar gauge pressure, with pump suction pressure maintained above 0.2 bar to prevent cavitation across the full engine load range. | interface-requirements | Interface Requirements |  | Test |  |  | Cavitation at pump inlet during high-speed engine operation is a known failure mode in standby diesel cooling circuits; the 0.2 bar suction minimum is derived from pump NPSH data and the circuit head loss at maximum flow. Loss of this interface during a LOOP event would cause engine overtemperature within minutes. | interface, engine-cooling, sil-2, session-591
IFC-REQ-023 | The interface between the Engine Pre-heat System and the Engine Jacket Water Circuit SHALL maintain standby jacket water temperature at ≥35°C using a 3 kW electric immersion heater circuit controlled by a thermostat with ±2°C hysteresis, supplied from the station UPS to remain active during AC blackout conditions. | interface-requirements | Interface Requirements |  | Demonstration |  |  | The pre-heat circuit must operate during blackout to maintain start readiness — this is precisely the scenario in which the EDG is required. AC supply from the UPS (rather than normal supply) ensures the heater remains energised during the bus blackout that triggers the EDG start demand. The ±2°C thermostat hysteresis prevents rapid cycling that degrades the heater element. | interface, engine-cooling, sil-2, session-591
IFC-REQ-024 | The interface between the Thermostatic Control Valve and the Radiator/Heat Exchanger SHALL route hot-side coolant flow to the heat exchanger at 0% to 100% of pump flow as a linear function of jacket water temperature between 75°C (full bypass) and 82°C (full radiator flow), with valve stroke response time not exceeding 5 seconds. | interface-requirements | Interface Requirements |  | Test |  |  | A 5-second stroke response is required to prevent the coolant temperature overshooting the 85°C upper limit during load step changes; faster valves introduce hunting. The 75–82°C operating band is set to provide a 10°C margin above the 75°C warm-up floor and a 3°C margin below the 85°C operating limit. | interface, engine-cooling, sil-2, session-591
IFC-REQ-025 | The interface between the Engine Cooling System and the EDG Instrumentation and Control System SHALL provide two independent 4-20 mA Pt100 temperature signals from the jacket water outlet header, a hardwired discrete trip output on cooling loss (active low, fail-safe), and a 4-20 mA coolant pressure signal, all routed on SIL 2 qualified cable with physical segregation from non-safety circuits. | interface-requirements | Interface Requirements |  | Inspection |  |  | Two independent temperature signals provide 1-of-2 voting logic in the I&C system for the engine overtemperature trip, consistent with IEC 61511 SIL 2 diagnostic coverage requirements. The fail-safe active-low trip output ensures that loss of signal (cable break) defaults to the safe state (engine trip). Physical segregation is required by BS EN 61000 (Electromagnetic compatibility) to prevent I&C trip spurious actuation from EMI generated by engine ignition circuits. | interface, engine-cooling, sil-2, safety-critical, session-591
IFC-REQ-026 | The interface between the Fuel Transfer Pump and the Day Tank SHALL deliver fuel at a minimum transfer rate of 50 L/min from the Bulk Storage Tank, controlled by a float-switch level signal from the Day Tank Level Control and Alarm unit, with transfer pump status (running/fault) monitored by the EDG I&C system. | interface-requirements | Interface Requirements |  | Test |  |  | 50 L/min transfer rate is derived from the Day Tank volume and the 30-minute refill requirement in SUB-REQ-048; lower rates risk delayed refill that allows the Day Tank to reach the low-fuel alarm threshold before transfer completes. Pump status monitoring is required for operator awareness during sustained LOOP events. | interface, fuel-oil, sil-2, session-591
IFC-REQ-027 | The interface between the Day Tank and the engine fuel injection system SHALL provide a continuous, uninterrupted fuel supply at 0.3 bar to 0.7 bar gauge with fuel temperature maintained between 10°C and 40°C to ensure fuel viscosity remains within the OEM injection pump specification throughout the engine operating range. | interface-requirements | Interface Requirements |  | Test |  |  | Fuel temperature limits are required because marine diesel viscosity varies by a factor of three between -5°C and 50°C; at the extremes, pump volumetric efficiency and atomisation quality degrade to the point where governor control authority is insufficient to maintain rated frequency. Tank heating and insulation are required in the EDG building HVAC design to maintain the 10°C lower limit at the -10°C ambient design minimum. | interface, fuel-oil, sil-2, session-591
IFC-REQ-028 | The interface between the Fuel Oil Strainer and Filter Assembly and the engine fuel injection system SHALL provide clean fuel at ISO 4406 ≤16/13/10, with differential pressure measurement across the filter element transmitted as a 4-20 mA signal to the EDG I&C panel, and a mechanical bypass valve set to open at 1.0 bar differential to protect the injection pump in the event of filter blockage. | interface-requirements | Interface Requirements |  | Inspection |  |  | The bypass valve protects the injection pump from starvation caused by a blocked filter during an unattended LOOP event. The bypass set-point of 1.0 bar is set above the 0.5 bar alarm threshold (SUB-REQ-047) to allow the alarm to trigger before bypass occurs, so the shift supervisor can initiate maintenance before unfiltered fuel reaches the injectors. | interface, fuel-oil, sil-2, session-591
STK-REQ-001 | The Emergency Diesel Generator system SHALL provide the control room operator with continuous real-time display of EDG operating parameters including output power (kW), frequency (Hz), terminal voltage (V), lubricating oil pressure, and engine coolant temperature. | stakeholder-requirements | Stakeholder Requirements |  | Demonstration | 100 |  | Control Room Operator, LOOP Response scenario: operator monitors EDG from desk displays showing kW, frequency, oil pressure, coolant temp to verify EDG is supplying safety loads correctly. | stakeholder, stk-control-room-operator, session-570, idempotency:stk-cro-display-570
STK-REQ-002 | The Emergency Diesel Generator system SHALL enable the control room operator to manually start, stop, and authorise load transfers for each EDG train from the main control room. | stakeholder-requirements | Stakeholder Requirements |  | Demonstration | 100 |  | Control Room Operator, LOOP Response scenario: operator initiates fast start and authorises transfer back to grid. Surveillance Test scenario: operator initiates fast start from control room. | stakeholder, stk-control-room-operator, session-570, idempotency:stk-cro-manual-570
STK-REQ-003 | The Emergency Diesel Generator system SHALL annunciate all abnormal EDG conditions as distinct alarms in the main control room within 2 seconds of detection. | stakeholder-requirements | Stakeholder Requirements |  | Test | 100 |  | Control Room Operator, EDG Failure to Start scenario: alarm 'EDG-A FAIL TO START' annunciates immediately so operator can verify Train B is carrying loads and initiate LCO entry. | stakeholder, stk-control-room-operator, session-570, idempotency:stk-cro-alarm-570
STK-REQ-004 | The Emergency Diesel Generator system SHALL provide sufficient information to the shift supervisor to support Limiting Condition for Operation entry and exit decisions, including EDG operability status and allowed outage time tracking. | stakeholder-requirements | Stakeholder Requirements |  | Demonstration | 86 |  | Shift Supervisor, EDG Failure to Start scenario: supervisor must enter LCO 3.8.1 with 72-hour restoration window. Trip During Operation scenario: supervisor re-evaluates allowed outage time with one EDG lost. | stakeholder, stk-shift-supervisor, session-570, idempotency:stk-ss-lco-570
STK-REQ-005 | The Emergency Diesel Generator system SHALL support implementation of station blackout emergency operating procedures, including load shedding prioritisation and connection of portable backup power sources. | stakeholder-requirements | Stakeholder Requirements |  | Demonstration | 100 |  | Shift Supervisor, Station Blackout scenario: shift supervisor implements SBO EOP, deploys portable pump, coordinates mobile diesel generator connection. System must support this response. | stakeholder, stk-shift-supervisor, session-570, idempotency:stk-ss-sbo-570
STK-REQ-006 | The Emergency Diesel Generator system SHALL enable fault diagnosis through locally accessible instrumentation and test points, permitting on-site repair by mechanical maintenance personnel. | stakeholder-requirements | Stakeholder Requirements |  | Inspection | 100 |  | Mechanical Technician, EDG Failure to Start scenario: mechanic dispatched to EDG building, diagnoses stuck fuel rack solenoid, replaces component. Requires accessible instrumentation for diagnosis. | stakeholder, stk-mechanical-technician, session-570, idempotency:stk-mech-diag-570
STK-REQ-007 | The Emergency Diesel Generator system SHALL support safe maintenance isolation through lock-out/tag-out provisions on all energy sources including fuel, electrical, compressed air, and cooling water. | stakeholder-requirements | Stakeholder Requirements |  | Inspection | 100 |  | Mechanical Technician, Planned Major Maintenance scenario: formal LOTO applied — fuel isolated, batteries disconnected, start air vented. All energy sources require isolation capability. | stakeholder, stk-mechanical-technician, session-570, idempotency:stk-mech-loto-570
STK-REQ-008 | The Emergency Diesel Generator system SHALL support calibration and functional testing of all protection and control instrumentation without requiring EDG operation or compromising safety system availability. | stakeholder-requirements | Stakeholder Requirements |  | Demonstration | 100 |  | I&C Technician, Surveillance Test and Maintenance scenarios: I&C technician calibrates sensors and troubleshoots protection systems. Must be possible without taking EDG out of service unnecessarily. | stakeholder, stk-ic-technician, session-570, idempotency:stk-ic-cal-570
STK-REQ-009 | The Emergency Diesel Generator system SHALL provide diagnostic access to control system parameters and protection setpoints for troubleshooting by qualified I&C personnel. | stakeholder-requirements | Stakeholder Requirements |  | Demonstration | 100 |  | I&C Technician, EDG Failure to Start and Trip scenarios: technician troubleshoots control/protection system faults. Requires access to parameters, setpoints, and fault history. | stakeholder, stk-ic-technician, session-570, idempotency:stk-ic-diag-570
STK-REQ-010 | The Emergency Diesel Generator system SHALL demonstrate compliance with ONR Safety Assessment Principles (SAPs) for engineered safety features, including diversity, redundancy, and independence requirements. | stakeholder-requirements | Stakeholder Requirements |  | Analysis | 100 |  | ONR, all scenarios: ONR provides regulatory approval of the safety case and inspects compliance with SAPs. The EDG as a Class 1 safety system must meet SAP targets for reliability and independence. | stakeholder, stk-onr, session-570, idempotency:stk-onr-sap-570
STK-REQ-011 | The Emergency Diesel Generator system SHALL maintain a deterministic safety case demonstrating that the EDG fulfils its nuclear safety function under all design basis conditions, as required by UK nuclear site licence conditions. | stakeholder-requirements | Stakeholder Requirements |  | Analysis | 100 |  | ONR, all scenarios: site licence conditions require a living safety case. The EDG safety case must cover all design basis events including LOOP, SBO, seismic, and common cause failure. | stakeholder, stk-onr, session-570, idempotency:stk-onr-safetycase-570
STK-REQ-012 | The Emergency Diesel Generator system SHALL achieve a start-on-demand reliability of at least 0.975 and a 24-hour mission reliability of at least 0.999, demonstrable through surveillance testing records. | stakeholder-requirements | Stakeholder Requirements |  | Analysis | 100 |  | Licensee, all scenarios: the licensee bears ultimate safety responsibility. Reliability targets from the probabilistic safety assessment define the minimum performance the EDG must demonstrate. | stakeholder, stk-licensee, session-570, idempotency:stk-licensee-reliability-570
STK-REQ-013 | The Emergency Diesel Generator system SHALL maintain complete qualification evidence, maintenance records, and modification history traceable to the original design basis throughout the plant operating life. | stakeholder-requirements | Stakeholder Requirements |  | Inspection | 100 |  | Licensee, Planned Maintenance scenario: quality records archived after overhaul. Documentation must demonstrate continued qualification through life — ONR can inspect at any time. | stakeholder, stk-licensee, session-570, idempotency:stk-licensee-docs-570
STK-REQ-014 | The Emergency Diesel Generator system SHALL accommodate OEM-specified maintenance regimes and accept qualified replacement parts without invalidating the safety case or equipment qualification. | stakeholder-requirements | Stakeholder Requirements |  | Analysis | 100 |  | EDG OEM, Planned Maintenance scenario: 5-yearly overhaul uses OEM work package (replace injectors, valve adjustment, turbo inspection). Maintenance regime must align with OEM requirements. | stakeholder, stk-oem, session-570, idempotency:stk-oem-maint-570
STK-REQ-015 | The Emergency Diesel Generator system SHALL prevent failure of backup power supply from contributing to an uncontrolled release of radioactive material, by providing sufficient redundancy and diversity in standby power sources. | stakeholder-requirements | Stakeholder Requirements |  | Analysis | 86 |  | Local Community: the community's fundamental expectation is that the nuclear site prevents accidents. The EDG is the last line of defence against station blackout leading to core damage and radioactive release. | stakeholder, stk-local-community, session-570, idempotency:stk-community-safety-570
STK-REQ-016 | The Emergency Diesel Generator system SHALL remain functional during and after a design basis earthquake of 0.2g peak ground acceleration, as required by Seismic Category I qualification per EUR requirements. | stakeholder-requirements | Stakeholder Requirements |  | Analysis | 100 |  | Operating Environment, Seismic constraint: the EDG must survive the design basis earthquake and start afterward if needed. Seismic qualification is a fundamental safety requirement for UK nuclear sites. | stakeholder, stk-environment, session-570, idempotency:stk-env-seismic-570
STK-REQ-017 | The Emergency Diesel Generator system SHALL operate across the full ambient temperature range of -10°C to +40°C and withstand a coastal salt-laden atmosphere without degradation of safety function. | stakeholder-requirements | Stakeholder Requirements |  | Test | 100 |  | Operating Environment: UK coastal nuclear sites experience temperature extremes and salt-laden air. EDG must start and run reliably at temperature extremes and resist corrosion from marine atmosphere. | stakeholder, stk-environment, session-570, idempotency:stk-env-climate-570
STK-REQ-018 | The Emergency Diesel Generator system SHALL not produce electromagnetic interference that could cause spurious actuation of co-located safety-related instrumentation and control systems, per IEC 61000-4 (Electromagnetic compatibility — testing and measurement techniques) series requirements. | stakeholder-requirements | Stakeholder Requirements |  | Test | 86 |  | Operating Environment, EMC constraint: the EDG shares a site with sensitive nuclear safety I&C. EMI from EDG starting or running must not cause spurious reactor protection system actuation. | stakeholder, stk-environment, session-570, idempotency:stk-env-emc-570
SUB-REQ-001 | The Diesel Engine Assembly SHALL achieve self-sustaining engine rotation within 3 seconds of receiving a start signal from the Starting Air System, with cylinder firing confirmed by all cylinders contributing to power output within 5 seconds, to support delivery of rated generator output within the 10-second system requirement. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | The 10-second system start requirement (SYS-REQ-001) is decomposed across the start chain: Starting Air System cranks the engine (0-3s), engine achieves self-sustaining combustion (3-5s), engine accelerates to rated speed and Synchronous Generator reaches rated voltage (5-10s). The 3-second self-sustain budget is consistent with medium-speed diesel cranking at 750 rpm with pre-heated coolant (>10°C). If self-sustaining rotation is not achieved within this window, an automatic start retry is required — not possible within the 10-second window without exceeding air receiver start attempt budget. | subsystem, diesel-engine-assembly, sil-3, session-571, idempotency:sub-dea-start-performance-571
SUB-REQ-002 | The Diesel Engine Assembly SHALL maintain engine speed within 750 rpm ±1.5 rpm (±0.2%) in steady-state operation under all loads from 0% to 110% rated power, and within 750 rpm ±22.5 rpm (±3%) during transient load steps of up to 30% rated power applied or removed in under 1 second. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | The generator output frequency tolerance of 50 Hz ±2% (SYS-REQ-006) maps to engine speed 750 ±15 rpm for a 4-pole generator. The ±1.5 rpm steady-state budget leaves margin for the isochronous governor droop and generator slip. The ±3% transient budget accommodates the governor's response time before the fuel rack settles; IEC 60034-1 allows transient ±10% frequency excursion if recovery is within 5 seconds. The 30% step load case reflects connection of the largest individual safety load (ECCS pump motor) during load sequencing. | subsystem, diesel-engine-assembly, sil-3, session-571, idempotency:sub-dea-speed-stability-571
SUB-REQ-003 | The Diesel Engine Assembly SHALL sustain continuous mechanical power output at 100% rated brake mean effective pressure for a minimum of 720 hours (30 days) between major maintenance interventions, consistent with a 24-hour mission reliability of 0.999 per demand. | subsystem-requirements | Subsystem Requirements |  | Analysis | 86 |  | The 30-day between-overhaul endurance requirement derives from the nuclear site's fuel storage capability (SYS-REQ-026: 7-day minimum at 100% load), post-accident monitoring requirements, and refuelling interval planning. MTBF data from qualified medium-speed nuclear diesels (e.g., PAXMAN, MAN, CATERPILLAR nuclear-grade) show B10 lives exceeding 5,000 hours for pistons, liners and bearings at rated BMEP; 720 hours represents a conservative continuous run mission within this envelope. Failure to sustain 24h continuous operation would invalidate the mission reliability figure of 0.999. | subsystem, diesel-engine-assembly, sil-3, session-571, idempotency:sub-dea-endurance-571
SUB-REQ-004 | The Engine Protection Relay Package SHALL detect engine overspeed exceeding 863 rpm (115% of rated 750 rpm), and SHALL trip the Diesel Fuel Injection System fuel rack to the minimum position within 1 second of setpoint crossing, independent of the digital control system. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Overspeed is hazard H-001 in the EDG hazard register — uncontrolled acceleration to destructive speed (>1,200 rpm) can cause catastrophic engine failure including crankcase fragmentation, with potential for radioactive release if co-located safety systems are damaged. The 115% trip setpoint is the nuclear industry standard per IEEE Std 741 (Standard Criteria and Guidelines for the Design, Installation, and Qualification of Emergency Diesel Generators); the 1-second response time ensures the engine is stopped before the mechanical runaway speed range of 130% rated is reached. The hardwired relay implementation ensures this function is immune to digital system faults per ARC-REQ-002 (hardware/software diversity). | subsystem, diesel-engine-assembly, sil-3, safety-trip, session-571, idempotency:sub-dea-overspeed-trip-571
SUB-REQ-005 | The Engine Protection Relay Package SHALL detect engine lubricating oil pressure below 2.0 bar at the main oil gallery, and SHALL initiate an engine trip within 2 seconds of setpoint crossing, with a pre-trip alarm annunciated to the Main Control Room at 2.5 bar. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Low lubricating oil pressure causes hydrodynamic bearing film collapse within 2-5 seconds of pressure loss, leading to metallic contact, bearing seizure, and crankshaft failure (hazard H-003). The 2.0 bar trip setpoint is established by OEM bearing film requirements at rated speed; 2.5 bar alarm provides 30-60 seconds of operator warning before the trip, consistent with IEEE Std 741. The 2-second trip response must be faster than the bearing-film collapse time to prevent irreversible damage. The pre-trip alarm supports Limiting Condition for Operation assessment by the shift supervisor (STK-REQ-004). | subsystem, diesel-engine-assembly, sil-3, safety-trip, session-571, idempotency:sub-dea-lop-trip-571
SUB-REQ-006 | The Engine Protection Relay Package SHALL detect engine jacket water coolant temperature exceeding 90°C at the cylinder head outlet, and SHALL initiate an engine trip within 2 seconds of setpoint crossing, with a pre-trip alarm annunciated at 85°C. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Jacket water temperature exceeding 90°C risks coolant boiling with consequent loss of cooling flow and rapid piston seizure (hazard H-006, SIL 2 per the hazard register). The 90°C trip setpoint is at least 10°C below the coolant boiling point at system pressure (typically 110°C at 1.5 bar system pressure), providing margin for continued heat rejection before coolant vaporises. The 85°C alarm setpoint gives operators 2-5 minutes of warning at typical heat-up rates. Consistent with vendor qualification data and IEEE Std 741 guidance for diesel engine protection. | subsystem, diesel-engine-assembly, sil-3, safety-trip, session-571, idempotency:sub-dea-hct-trip-571
SUB-REQ-007 | The Diesel Fuel Injection System SHALL meter fuel delivery with a maximum cylinder-to-cylinder variation of ±3% of mean fuel quantity per injection event, measured under steady-state rated load conditions, to ensure balanced combustion and prevent individual cylinder thermal overload. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Cylinder-to-cylinder fuel imbalance exceeding ±5% causes differential cylinder thermal loading, accelerated liner wear, and uneven power contribution to the crankshaft — increasing vibration and fatigue loading of the crankshaft (linked to catastrophic failure hazard H-001). The ±3% requirement provides a 2× margin below the OEM tolerance for injection pump wear and is consistent with nuclear-grade diesel maintenance practice. Verification by combustion analyser during pre-operational surveillance testing per Technical Specification monthly test (SYS-REQ-013 / STK-REQ-008). | subsystem, diesel-engine-assembly, sil-3, session-571, idempotency:sub-dea-fuel-metering-571
SUB-REQ-008 | The Diesel Engine Assembly, including all sub-components and their mounting interfaces, SHALL be qualified to remain functional during and after a seismic event with a peak ground acceleration of 0.2g and response spectra consistent with EUR Seismic Category I requirements, with no loss of rated power delivery capability post-event. | subsystem-requirements | Subsystem Requirements |  | Analysis | 86 |  | EDG seismic qualification is required by nuclear site licence conditions and ONR Safety Assessment Principles for Seismic Category I equipment per EUR Document EUR 001 Rev. D. The 0.2g PGA represents the UK design basis earthquake for modern nuclear sites; earlier UK sites may use lower values per site-specific PSA. Qualification must cover the engine block mounting bolts (moment loading during horizontal excitation), the turbocharger (cantilevered mass), and the generator coupling alignment (relative displacement). Failure of EDG during the design basis earthquake when offsite power may also be lost represents a simultaneous loss of all AC power sources — a cliff-edge risk to reactor safety. | subsystem, diesel-engine-assembly, sil-3, session-571, idempotency:sub-dea-seismic-571
SUB-REQ-009 | When any Engine Protection Relay Package trip setpoint is exceeded, the Diesel Engine Assembly SHALL transition to its safe state (all fuel injection ceased, crankshaft deceleration to standstill) within 5 seconds of the trip signal, with no manual operator action required. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Safe state for the Diesel Engine Assembly is defined as 'engine stopped with no fuel flow' — the fail-safe condition for all four protection trip functions (overspeed, high coolant temp, low oil pressure, overcurrent). The 5-second transition time encompasses the worst-case governor response, fuel rack travel to minimum stop, and engine deceleration from 115% rated speed to rest (kinetic energy decay at no-load). This safe state is consistent with IEC 61508 (Functional safety of E/E/PE safety-related systems) safe state analysis for SIL 3 protection functions and eliminates the hazardous condition before it can escalate to structural damage. | subsystem, diesel-engine-assembly, sil-3, safety-trip, safe-state, session-571, idempotency:sub-dea-safe-state-571
SUB-REQ-010 | The Electrical Switchgear and Load Sequencer Subsystem SHALL implement a priority-based load sequencer that connects safety loads to the 6.6kV emergency bus in a fixed priority sequence within 10 seconds of generator breaker closure, with each load group delayed by a minimum of 500ms to prevent simultaneous inrush currents from exceeding generator transient overload capacity. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | SYS-REQ-003 requires connection of safety loads via a priority-based load sequencer. The 500ms inter-group delay prevents cumulative inrush currents (typically 6× FLA per motor) from exceeding the generator's short-time overload rating during the critical bus restoration sequence following a LOOP event. This timing is consistent with IEEE 387 load-acceptance test criteria. | session-572, qc, switchgear-load-sequencer, idempotency:sub-els-load-sequencer-572
SUB-REQ-011 | The Fuel Oil System SHALL maintain at least 7,000 litres usable fuel per EDG train across day tanks and bulk storage, meeting CIMAC Class DM specification, sustaining rated-load operation for 7 days. | subsystem-requirements | Subsystem Requirements |  | Inspection | 71 |  | SYS-REQ-008 requires 7-day fuel storage capacity. At rated output of a typical nuclear EDG (approximately 2-4 MW), fuel consumption is approximately 800-1200 litres/hour; 7,000 litres per day times 7 days = 49,000 litres minimum. Day tank sizing of 750-1,000 litres provides 1-hour autonomous operation; bulk tank supplies replenishment via transfer pump. CIMAC Class DM is the UK nuclear industry fuel specification for safety-related diesel engines. | session-572, qc, fuel-oil-system, idempotency:sub-fos-fuel-storage-572, reqs-eng-session-583
SUB-REQ-012 | The Engine Protection Relay Package SHALL implement a fail-safe de-energise-to-trip relay architecture such that loss of 125VDC control power to any trip relay automatically initiates engine trip to standstill, with a hardware-keyed maintenance inhibit that requires physical key insertion at the relay panel to suppress any individual trip function for maintenance, and automatically cancels on key removal. | subsystem-requirements | Subsystem Requirements |  | Demonstration | 86 |  | IEC 61513 (Nuclear power plants — Instrumentation and control systems — General requirements for systems) requires safety-related I&C to fail safe. The engine protection relay package classified as Functionally Autonomous (hex D6B73858) requires explicit fail-safe mode definition: de-energise-to-trip ensures DC power loss does not disable protection. The hardware-keyed inhibit (as opposed to software override) prevents cyber attack from disabling engine protection and ensures every inhibit is traceable to a physical human action per ONR SAPs. Without this, the relay package can be de-feated remotely. | session-580, qc, engine-protection, fail-safe, sil-3, idempotency:sub-eprp-failsafe-override-580
SUB-REQ-013 | The Diesel Fuel Injection System SHALL operate from a dedicated 24VDC Class 1E power supply with supply voltage maintained within 24VDC ±10% across all load conditions, with a minimum 4-hour battery-backed autonomy for the fuel injection control module independent of engine cranking loads, to ensure injection function is sustained during EDG start transients and any short-duration DC bus disturbances. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | The diesel fuel injection system is classified as Powered (hex D6D53218, bit 4), requiring explicit power source, voltage range, and consumption requirements per the UHT classification. At nuclear sites, all safety-related powered equipment must have a defined Class 1E power source per IEEE 308 (Criteria for Class 1E Electric Systems for Nuclear Power Generating Stations). The 24VDC ±10% tolerance ensures electronic fuel injection control modules remain within operating specification during DC bus voltage excursions under LOOP conditions. Without a defined power budget, injection failure during a fault-initiated trip creates an unverifiable failure mode. | session-580, qc, fuel-injection, power-supply, class-1e, idempotency:sub-fuel-injection-power-580
SUB-REQ-014 | The Starting Air System Air Receiver Banks (A and B) SHALL each maintain a minimum stored pressure of 25 bar and a maximum operating pressure of 30 bar, providing sufficient capacity for a minimum of three consecutive start attempts at 20°C ambient. | subsystem-requirements | Subsystem Requirements |  | Test | 71 |  | IEC 61508 (Functional safety of E/E/PE safety-related systems) SIL 3 start function requires redundant air trains. Three start attempts is the ONR-mandated minimum to account for false cranks. 25 bar minimum is the minimum inlet pressure required by the air start distributor valve to achieve the cranking torque needed to overcome diesel engine compression at cold soak (10°C). Derived from SYS-REQ-004 (start reliability 0.975 per demand) — insufficient air receiver capacity is the primary single cause of failed start attempts. | subsystem, starting-air-system, sil-3, session-581, idempotency:sub-sas-receivers-pressure-581
SUB-REQ-015 | The Starting Air System Air Start Valve and Distribution Manifold SHALL fully open and deliver compressed air to all engine cylinders within 0.5 seconds of receiving an electrical start command from the EDG Instrumentation and Control System. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | The 3-second self-sustaining combustion budget (SUB-REQ-001) requires that cranking air reaches the cylinders within 0.5 s of start signal to allow sufficient compression-ignition cycles before the 3-second window expires. Valve actuation latency is the dominant timing contributor in the start chain from signal to first compression stroke. Verified by instrumented start test measuring solenoid energisation to first cylinder pressure rise. | subsystem, starting-air-system, sil-3, session-581, idempotency:sub-sas-startvalve-actuation-581
SUB-REQ-016 | The Starting Air System Air Compressor and Recharge Unit SHALL restore both Air Receiver Banks from a post-three-attempt low (minimum 20 bar) to full operating pressure of 30 bar within 30 minutes of start completion. | subsystem-requirements | Subsystem Requirements |  | Test | 100 |  | Technical Specifications for nuclear EDGs typically require the EDG to be returned to operability within one hour of a surveillance test. A 30-minute recharge allows 30 minutes for post-test inspection before the operability clock expires. Recharge time is driven by compressor capacity against receiver volume; 30 minutes corresponds to approximately 5 kW of compressor power for a 250-litre dual-receiver installation. | subsystem, starting-air-system, session-581, idempotency:sub-sas-compressor-recharge-581
SUB-REQ-017 | The Starting Air System Moisture Separator and Drain System SHALL maintain compressed air dewpoint at or below minus 40 degrees C at atmospheric pressure throughout the air receiver and distribution manifold. | subsystem-requirements | Subsystem Requirements |  | Inspection | 100 |  | Compressed air with dewpoint above minus 40 C risks liquid water formation in the air start distributor valve and manifold at the minimum site ambient temperature of 5 C. Water ingress to engine cylinders can cause hydraulic lock and crankshaft failure on cranking — a catastrophic failure mode that would prevent EDG start and require major engine overhaul. The minus 40 C threshold is derived from EN ISO 8573-1 Quality Class 3 and is consistent with nuclear plant instrument air specifications. | subsystem, starting-air-system, session-581, idempotency:sub-sas-moisture-dewpoint-581
SUB-REQ-018 | When Starting Air System receiver pressure drops to 27 bar on either bank, the Pressure Monitoring and Low-Pressure Alarm component SHALL generate a control room annunciation within 5 seconds. When pressure drops to 22 bar, the EDG Instrumentation and Control System SHALL inhibit further start attempts from that bank until pressure is restored to minimum 25 bar. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | 27 bar alarm provides operator time to investigate before reaching the 25 bar start minimum. 22 bar inhibit prevents a start attempt on insufficient air supply, which would cause a failed crank and consume remaining air without achieving engine rotation. The inhibit is the safe state for this failure mode per IEC 61508 SIL 3 requirements — a failed start with depleted air is worse than no start attempt. Aligns with SYS-REQ-010 (independent hardwired trip functions). | subsystem, starting-air-system, sil-3, safe-state, session-581, idempotency:sub-sas-lowpressure-alarm-581
SUB-REQ-019 | The EDG Instrumentation and Control System Automatic Start Logic Controller SHALL detect emergency bus undervoltage below 5.94 kV within 100 ms and issue an air start command to the Starting Air System within 200 ms of detection, confirmed by hardwired LOOP signal from the Plant Protection System. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | SYS-REQ-002 requires automatic start on bus undervoltage below 5.94 kV. The 100 ms detection budget is allocated to the I&C from the total 200 ms LOOP detection budget (SYS-REQ-002), with the remaining 100 ms allocated to the air start valve actuation (SUB-REQ-015). Hardwired confirmation from the Plant Protection System prevents spurious start on transient undervoltage. Derived from SYS-REQ-001 (10-second start) and SYS-REQ-002 (automatic LOOP start). | subsystem, ic-system, sil-3, session-581, idempotency:sub-ic-loop-detection-581
SUB-REQ-020 | The EDG Instrumentation and Control System Engine and Generator Protection Logic SHALL generate a de-energise-to-trip relay output within 200 ms of any monitored parameter exceeding its trip setpoint, and SHALL be designed to IEC 61508 Safety Integrity Level 3 with a Probability of Failure on Demand not exceeding 1x10 to the power minus 3. | subsystem-requirements | Subsystem Requirements |  | Analysis | 86 |  | 200 ms trip response is the maximum permissible latency before continued engine operation at overspeed, low oil pressure, or high coolant temperature would cause irreversible mechanical damage. This budget is consistent with medium-speed diesel protection practice and is tighter than the engine mechanical failure time constants (overspeed damage onset approximately 800 ms at 115 percent rated speed). SIL 3 PFD target of 1e-3 per demand derives from the nuclear site safety case requirement for EDG start reliability of at least 0.975 per demand (SYS-REQ-004), apportioning protection logic unavailability to 0.001. | subsystem, ic-system, sil-3, safety-critical, session-581, idempotency:sub-ic-protection-trip-response-581
SUB-REQ-021 | The EDG Instrumentation and Control System Qualified I/O Module Assembly SHALL provide Class 1E qualified electrical isolation of at least 1.5 kV RMS between safety-classified inputs and outputs and any non-Class-1E circuit, and SHALL maintain isolation integrity following a design basis seismic event of 0.3g PGA. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | IEC 60780 (Nuclear power plants - Electrical equipment of the safety system) and ONR SAP EKP.4 require Class 1E equipment to be electrically isolated from non-Class-1E circuits to prevent common-cause failure propagation. The 0.3g PGA seismic requirement derives from SYS-REQ-009. Loss of I/O isolation is a common-cause failure mode that could simultaneously disable both EDG trains by coupling a fault from the normal power distribution into the safety bus. | subsystem, ic-system, sil-3, seismic, session-581, idempotency:sub-ic-io-isolation-581
SUB-REQ-022 | The EDG Instrumentation and Control System Plant Communication Gateway SHALL be implemented as a unidirectional data diode transmitting EDG status data to the Main Control Room network, with no return data path capable of propagating a signal to the safety-classified I&C equipment. | subsystem-requirements | Subsystem Requirements |  | Inspection | 86 |  | SYS-REQ-012 requires safety-related control and protection systems to be isolated from non-safety networks. A unidirectional data diode is the only hardware-enforced implementation that prevents network-originated signals from reaching the safety bus. Bidirectional gateways with software-enforced isolation have been rejected as they introduce a shared-cause vulnerability where gateway compromise can propagate adversarial commands to the safety logic. Consistent with IEC 62645 (Nuclear power plants - Instrumentation and control systems - Requirements for security programmes). | subsystem, ic-system, sil-3, cybersecurity, session-581, idempotency:sub-ic-comms-gateway-isolation-581
SUB-REQ-023 | When the EDG Instrumentation and Control System Automatic Start Logic Controller detects a self-diagnostic fault in any SIL 3 function, the I&C System SHALL transition to a de-energised safe state within 500 ms, initiating engine protection trip and generating a control room fault alarm, while preserving the last-good EDG status data at the Annunciation and HMI Panel. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | IEC 61508 SIL 3 requires defined safe states for all safety function failures. The safe state for I&C logic failure is de-energise-to-trip (engine stopped) rather than latched-run, because an uncontrolled engine running without protection monitoring is the more dangerous failure mode. 500 ms transition budget is chosen to ensure the trip is complete before any monitored protection parameter would reach a damage threshold from the unprotected state. | subsystem, ic-system, sil-3, safe-state, session-581, idempotency:sub-ic-safe-state-581
SUB-REQ-024 | The Bus Undervoltage Sensing Relay SHALL detect 6.6kV emergency bus voltage below 4.6kV (70% nominal) sustained for more than 200ms and issue an EDG automatic start initiation signal within 200ms of threshold crossing, using two-out-of-three voting logic across three independent voltage transformer inputs. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | 200ms detection threshold is derived from the maximum permissible bus blackout time before safety systems (RCP seal injection, EFWS) deplete their Class 1E UPS reserves. The 4.6kV setpoint (70% nominal) discriminates credible LOOP from transient voltage dips caused by motor starts on the emergency bus. Two-out-of-three voting prevents spurious EDG starts on single VT failure while ensuring detection on dual-channel loss. Drives SYS-REQ-002. | subsystem, electrical-switchgear-and-load-sequencer, sil-3, safety-critical, session-582, idempotency:sub-swgr-buvr-loop-detection-582
SUB-REQ-025 | The Generator Circuit Breaker SHALL close onto the 6.6kV emergency bus within 100ms of receiving a close command from the Synchronising Check Relay (live-bus condition) or within 100ms of receiving a dead-bus close command, and SHALL trip open within 100ms of receiving a trip command from the Generator Electrical Protection Relay Package or from the I&C system emergency trip. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | 100ms close time is derived from the 10-second full bus restoration budget (SYS-REQ-001): generator acceleration 8s, GCB mechanical operation 0.1s, leaving margin for sequencer timing. 100ms trip time is the maximum permissible to limit fault energy on the emergency bus during a generator electrical fault; longer trip times risk thermal damage to bus conductors at 25kA fault level. Class 1E spring-charged mechanism provides deterministic operating time independent of DC supply voltage variation ±20%. | subsystem, electrical-switchgear-and-load-sequencer, sil-3, safety-critical, session-582, idempotency:sub-swgr-gcb-close-trip-time-582
SUB-REQ-026 | The Synchronising Check Relay SHALL permit Generator Circuit Breaker closure only when EDG output voltage is within ±10% of 6.6kV, frequency is within ±0.5Hz of 50Hz, and phase angle difference is within ±10 degrees, and SHALL issue an unconditional dead-bus close permission when bus voltage is below 20% of nominal (1.32kV) for more than 500ms without requiring frequency or phase angle synchronisation. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | ±10% voltage and ±0.5Hz frequency windows represent the limits within which out-of-phase closing transient currents remain below the generator's mechanical endurance rating (typically 3 per unit peak for 100ms). ±10 degree phase angle limit bounds the closing transient to less than 0.5 per unit. Dead-bus override threshold of 20% nominal ensures the relay distinguishes a truly de-energised bus (LOOP condition requiring immediate connection) from a very low-voltage live bus. Without the dead-bus override the EDG could not connect during a LOOP, defeating its safety function. | subsystem, electrical-switchgear-and-load-sequencer, sil-3, safety-critical, session-582, idempotency:sub-swgr-sync-check-relay-582
SUB-REQ-027 | The Generator Electrical Protection Relay Package SHALL provide differential protection (87G) with a minimum operating current of 10% rated generator current, overcurrent protection (51) with time-inverse characteristic, loss-of-excitation protection (40) with offset-mho impedance characteristic, and reverse power protection (32) with 2% of rated power pickup, each issuing an independent hardwired trip signal to the Generator Circuit Breaker within 100ms of fault detection. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | The 87G minimum operating threshold of 10% rated current detects internal generator faults while remaining insensitive to CT mismatch (typically 1-2%). Loss-of-excitation (40) protection prevents generator motoring and loss of reactive power support to the safety bus, which would cause bus voltage collapse. Reverse power (32) at 2% pickup detects engine failure with the generator motoring from the bus. Each protection function is independent per IEEE C37.102 (Guide for AC Generator Protection) to prevent common-cause failure disabling all electrical protection. Hardwired trip path ensures operation independent of I&C system availability. | subsystem, electrical-switchgear-and-load-sequencer, sil-3, safety-critical, session-582, idempotency:sub-swgr-gen-elec-protection-582
SUB-REQ-028 | When the Generator Electrical Protection Relay Package detects a protection trip condition or when the Class 1E Switchgear Control Power Supply falls below 95VDC, the Electrical Switchgear and Load Sequencer Subsystem SHALL open the Generator Circuit Breaker within 200ms and inhibit all close commands until the fault condition is cleared and a manual reset is performed by a licensed operator. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Safe state requirement per IEC 61508 (Functional safety of E/E/PE safety-related systems) for SIL 3 subsystem. Generator electrical fault requires immediate isolation to prevent propagation to the Class 1E emergency bus. 200ms safe state transition time allows for GCB mechanical operation (100ms) plus protection relay operate time (100ms). Control power undervoltage at 95VDC (76% of 125VDC nominal) ensures the GCB trip coil receives sufficient energy for reliable operation even at battery end-of-discharge. Manual reset requirement prevents automatic reconnection after a fault, requiring a licensed operator to assess cause and authorise restart per nuclear site licence condition. | subsystem, electrical-switchgear-and-load-sequencer, sil-3, safe-state, safety-critical, session-582, idempotency:sub-swgr-safe-state-582
SUB-REQ-029 | The EDG Building and Support Systems SHALL incorporate an automatic gaseous total-flood fire suppression system (HFC-227ea or CO2 with pre-discharge alarm) rated to extinguish a Class B diesel fuel fire within 30 seconds of actuation, with a two-hour fire-rated separation barrier between Train A and Train B EDG rooms to maintain operability of the alternate train during a single-train fire event. | subsystem-requirements | Subsystem Requirements |  | Inspection |  |  | SYS-REQ-011 derives from hazard H-004 (fire in EDG building, SIL 2). The 30-second suppression criterion is taken from NFPA 750 (Standard on Water Mist Fire Protection Systems) and BS EN 15004 (Fixed firefighting systems — Gas extinguishing systems) for unattended machinery spaces with flammable liquid hazards. The two-hour barrier rating satisfies BS 476 Part 22 (Fire tests on building materials and structures) for Class B fire separation between redundant safety-classified rooms, ensuring that a single fire event cannot disable both EDG trains simultaneously. | session-585, qc, edg-building, fire-protection, sil-2, idempotency:sub-building-fire-585
SUB-REQ-030 | The Category 1 Building Structure SHALL maintain structural integrity and continue to house and protect all installed EDG equipment during and following a design basis earthquake of 0.2g PGA, with no structural deformation exceeding 10mm at any equipment anchor point. | subsystem-requirements | Subsystem Requirements |  | Test |  |  | SYS-REQ-009 requires EDG operability at 0.2g PGA; the building is the primary seismic protection boundary. The 10mm anchor-point deformation limit is derived from engine skid anchor bolt clearance tolerances specified by the engine OEM to prevent bearing misalignment during post-seismic operation. Seismic Category I classification follows BS EN 1998-1 and ONR Safety Assessment Principles. | subsystem, edg-building, sil-2, seismic, session-586, idempotency:sub-building-seismic-struct-586
SUB-REQ-031 | The Category 1 Building Structure SHALL provide physical separation between EDG trains by a minimum 2-hour rated fire barrier, such that a design basis fire in one train enclosure cannot propagate to the redundant train enclosure. | subsystem-requirements | Subsystem Requirements |  | Inspection |  |  | SYS-REQ-007 requires two independent redundant trains; SYS-REQ-011 requires fire barriers maintaining alternate train operability. The 2-hour fire rating is derived from UK ONR technical guidance on nuclear fire safety and the maximum credible fire duration in an EDG enclosure containing a 4,000L fuel day tank. Physical train separation is preferred over shared space with fire barriers alone, as it eliminates common-cause fire-suppression-agent discharge scenarios. | subsystem, edg-building, sil-2, fire, session-586, idempotency:sub-building-train-sep-586
SUB-REQ-032 | The Ventilation and Combustion Air System SHALL supply a minimum of 0.55 kg/s of combustion air per MW of rated engine output at an inlet temperature not exceeding 40°C and maintain engine room ambient temperature below 45°C during continuous full-load operation. | subsystem-requirements | Subsystem Requirements |  | Test |  |  | The 0.55 kg/s per MW combustion air figure is derived from the engine manufacturer's fuel-air ratio at rated output plus 10% margin for combustion efficiency degradation over service life. The 45°C engine room limit is the upper ambient limit specified in the engine qualification envelope; exceedance causes derating of the turbocharger and reduces start-on-demand margin. The inlet 40°C limit reflects the UK nuclear site extreme summer ambient design temperature per CIBSE Guide A. | subsystem, edg-building, sil-2, hvac, session-586, idempotency:sub-building-hvac-airflow-586
SUB-REQ-033 | When the EDG receives an automatic start signal, the Ventilation and Combustion Air System SHALL initiate fan motor start within 5 seconds and achieve rated airflow within 30 seconds of the engine start signal. | subsystem-requirements | Subsystem Requirements |  | Test |  |  | SYS-REQ-001 requires the EDG to reach rated voltage within 10 seconds of start signal. The HVAC must reach rated airflow before the engine reaches rated speed at approximately 15-20 seconds. The 5-second fan start and 30-second rated airflow time allows the fan to be running when the engine reaches full combustion load, preventing thermal stress from inadequate air exchange during the critical ramp-up phase. | subsystem, edg-building, sil-2, hvac, session-586, idempotency:sub-building-hvac-start-586
SUB-REQ-034 | The Exhaust Silencer and Discharge Stack SHALL limit exhaust gas backpressure to not more than 50 mbar at the turbocharger outlet under all operating conditions from no-load to 110% rated load, and remain structurally intact following a design basis earthquake of 0.2g PGA. | subsystem-requirements | Subsystem Requirements |  | Test |  |  | The 50 mbar backpressure limit is specified by the diesel engine OEM as the maximum permissible backpressure for rated power output without turbocharger surge or thermal overloading. Exceedance reduces available output power and risks turbocharger damage; below this threshold the silencer can be designed for adequate noise attenuation. Seismic qualification prevents stack collapse blocking the exhaust and stalling the engine after the earthquake mission begins. | subsystem, edg-building, sil-2, exhaust, session-586, idempotency:sub-building-exhaust-back-586
SUB-REQ-035 | The Drain and Spill Containment System SHALL provide bunded containment with a minimum capacity of 110% of the largest single fluid inventory within the building (diesel day tank: 4,000 litres), with sump high-level alarm annunciation to the main control room within 60 seconds of breach detection. | subsystem-requirements | Subsystem Requirements |  | Inspection |  |  | The 110% bunded capacity rule follows UK Environment Agency Pollution Prevention Guidance PPG2 for above-ground oil storage. The 4,000L day tank is the dominant spill risk; containing 110% prevents secondary containment overflow under worst-case scenario. 60-second control room annunciation enables operator response before a spill migrates to an uncontained area, and derives from the same alarm response time budget used in the fire detection system design. | subsystem, edg-building, flood, sil-2, session-586, idempotency:sub-building-drain-cap-586
SUB-REQ-036 | When a Category 1 Building Structure breach is detected by the structural monitoring system, the EDG Building and Support Systems SHALL automatically isolate the affected train and generate a control room alarm within 30 seconds, while maintaining operability of the redundant train. | subsystem-requirements | Subsystem Requirements |  | Demonstration |  |  | SIL 2 safety function requires a defined safe state on failure. A structural breach (seismic damage, impact) that degrades protection for one train must not cascade to the redundant train. The 30-second alarm response time allows operators to take manual action before secondary effects (flooding, fire) propagate. This requirement implements the safe state for the EDG Building Structure SIL 2 function as required by IEC 61508 (Functional Safety of E/E/PE Safety-Related Systems). | subsystem, edg-building, sil-2, safe-state, session-586, idempotency:sub-building-safe-state-586
SUB-REQ-037 | The Engine Cooling System SHALL maintain engine jacket water outlet temperature within 75°C to 85°C during continuous operation at any load from 25% to 110% of rated power. | subsystem-requirements | Subsystem Requirements |  | Test |  |  | IEC 61508 SIL 2 derived from SYS-REQ-005. Jacket water temperature band of 75–85°C is the manufacturer-specified operating envelope for medium-speed 4-stroke diesel engines in standby duty; operation above 85°C degrades lubricant film viscosity and risks liner cavitation, while operation below 75°C increases fuel consumption and causes condensation-related cylinder corrosion. Failure to maintain this band during the 24-hour rated-load run risks premature engine failure. | subsystem, engine-cooling, sil-2, session-591
SUB-REQ-038 | While in standby, the Engine Cooling System SHALL maintain jacket water temperature at not less than 35°C using the Engine Pre-heat System to ensure the engine is capable of reaching rated speed within 10 seconds of start signal. | subsystem-requirements | Subsystem Requirements |  | Demonstration |  |  | Derived from SYS-REQ-001 (10-second start-to-rated-speed requirement). A cold engine at ambient -10°C has insufficient lubricant film and may fail to fire reliably; 35°C is the minimum jacket water temperature at which the OEM guarantees start reliability consistent with the 0.975 start-on-demand probability in SYS-REQ-004. Below 35°C, start transient torque and lube oil flow rates fall outside the OEM qualification envelope. | subsystem, engine-cooling, sil-2, session-591
SUB-REQ-039 | The Engine Cooling System SHALL dissipate engine thermal rejection at not less than 110% of rated thermal load at a maximum ambient temperature of 35°C without exceeding the jacket water temperature limit defined in SUB-REQ-036. | subsystem-requirements | Subsystem Requirements |  | Test |  |  | Derived from SYS-REQ-005 (24-hour continuous operation) and SYS-REQ-017 (35°C maximum ambient). The 110% margin accounts for fouling of the heat exchanger surface during extended operation and provides headroom against ambient temperature excursions. Without this margin, summer ambient conditions combined with heat exchanger fouling could cause sustained coolant temperature exceedance during multi-day operation in a LOOP event. | subsystem, engine-cooling, sil-2, session-591
SUB-REQ-040 | When jacket water outlet temperature exceeds 95°C or jacket water circuit pressure falls below 0.5 bar gauge, the Engine Cooling System SHALL generate a hardwired engine trip signal to the EDG Instrumentation and Control System within 200 milliseconds. | subsystem-requirements | Subsystem Requirements |  | Test |  |  | SIL 2 safe-state requirement derived from SYS-REQ-010 (hardwired engine trip circuits). The 95°C threshold is set 10°C above the 85°C upper operating limit to allow brief transients without spurious trip, while preventing sustained overtemperature that causes head gasket failure. The 0.5 bar pressure threshold detects coolant loss before dry-running engine damage occurs. The 200 ms trip response is required by IEC 61511 (Functional safety of SIS in the process industry) SIL 2 to ensure the safe state is reached before coolant system damage propagates to piston seizure. | subsystem, engine-cooling, sil-2, safety-trip, safe-state, session-591
SUB-REQ-041 | The Coolant Circulation Pump SHALL maintain a minimum coolant flow rate of 150 L/min at 0.8 bar differential pressure throughout the engine load range from 25% to 110% of rated power. | subsystem-requirements | Subsystem Requirements |  | Test |  |  | Derived from SYS-REQ-005. Flow rate of 150 L/min at 0.8 bar is determined by the OEM heat balance for a medium-speed diesel in this power range; below this flow, the jacket water outlet temperature differential across the engine block exceeds 10°C, creating thermal gradients that cause head distortion over extended operation. The pump is engine-driven, so performance must be verified across the full engine speed range. | subsystem, engine-cooling, sil-2, session-591
SUB-REQ-042 | The Thermostatic Control Valve SHALL modulate bypass coolant flow to maintain jacket water temperature within ±3°C of the 80°C setpoint during steady-state engine operation at rated load. | subsystem-requirements | Subsystem Requirements |  | Test |  |  | Derived from SYS-REQ-006 (voltage and frequency stability). Jacket water temperature stability directly affects fuel injection timing and cylinder firing consistency; a ±3°C band ensures combustion stability within the OEM governor envelope. Wider temperature excursions during steady-state operation indicate valve hysteresis and are a precursor to temperature hunting, which has caused premature valve failure in comparable standby diesel applications (UK nuclear site operating experience). | subsystem, engine-cooling, sil-2, session-591
SUB-REQ-043 | The Engine Cooling System pressure boundary, including the Engine Jacket Water Circuit, Coolant Circulation Pump, and Radiator/Heat Exchanger, SHALL remain leak-free and functional following a Design Basis Earthquake of 0.25g PGA as specified in SYS-REQ-009, with post-seismic coolant flow re-established within 30 seconds. | subsystem-requirements | Subsystem Requirements |  | Analysis |  |  | SIL 2 seismic requirement derived from SYS-REQ-009. The Engine Cooling System must survive the DBE because loss of cooling following a seismic event would prevent the EDG from fulfilling its post-earthquake safe shutdown function. Analysis (rather than test) is used because shake-table testing of a full cooling system assembly is impractical; seismic qualification by analysis per ASCE 4 (Seismic Analysis of Safety-Related Nuclear Structures) and IEEE 344 (Recommended practice for seismic qualification of Class 1E equipment for nuclear power generating stations) provides equivalent evidence. | subsystem, engine-cooling, sil-2, seismic, session-591
SUB-REQ-044 | The Fuel Oil System SHALL supply diesel fuel to the engine injection system at a pressure of 0.3 bar to 0.7 bar gauge and a flow rate sufficient for rated engine power output throughout the full 24-hour operating duration specified in SYS-REQ-005. | subsystem-requirements | Subsystem Requirements |  | Test |  |  | IEC 61511 SIL 2 derived from SYS-REQ-005. The 0.3–0.7 bar delivery pressure range is determined by the OEM fuel injection pump inlet specification; pressures outside this range cause either injector dribble (low pressure) or premature injection pump seal failure (high pressure). Flow rate adequacy at rated power must be demonstrated under fuel temperature extremes since viscosity variation of up to 20% affects pump volumetric efficiency. | subsystem, fuel-oil, sil-2, session-591
SUB-REQ-045 | The Bulk Storage Tank SHALL maintain a minimum fuel inventory of 110% of the 7-day fuel demand at 100% rated load as specified in SYS-REQ-008, with a high-level alarm at 95% fill and a low-level alarm at 20% fill providing warning before reserve depletion. | subsystem-requirements | Subsystem Requirements |  | Inspection |  |  | The 110% margin over the SYS-REQ-008 7-day inventory provides one day of additional reserve for extended LOOP events or unexpected consumption increases from abnormal engine loading. The alarm thresholds are set to provide sufficient time for a refuelling team to respond before approaching the minimum reserve, based on typical fuel delivery response times at UK nuclear sites (4–8 hours). | subsystem, fuel-oil, sil-2, session-591
SUB-REQ-046 | The Day Tank SHALL maintain a working inventory of not less than 4 hours of fuel at rated engine load to provide autonomous operation during a Bulk Storage Tank refuelling transfer interruption, with a low-level alarm at 60 minutes remaining inventory. | subsystem-requirements | Subsystem Requirements |  | Test |  |  | The 4-hour Day Tank autonomy decouples the engine from the Bulk Storage Tank transfer system, ensuring that a transfer pump failure or valve seizure does not immediately starve the engine. The 60-minute low-level alarm provides the operating crew sufficient time to initiate corrective action (transfer pump restart or backup transfer) before engine fuel starvation occurs. | subsystem, fuel-oil, sil-2, session-591
SUB-REQ-047 | The Fuel Oil Strainer and Filter Assembly SHALL maintain fuel particle contamination downstream of the filter element at ISO 4406 cleanliness code 16/13/10 or better under maximum flow conditions, with a differential pressure alarm at 0.5 bar indicating filter blockage requiring maintenance. | subsystem-requirements | Subsystem Requirements |  | Test |  |  | ISO 4406 cleanliness code 16/13/10 is the maximum fuel contamination level specified by the OEM for the injection pump and injector nozzles; exceeding this level causes accelerated injector wear and nozzle blockage that degrades fuel spray quality and reduces available power. The 0.5 bar differential pressure alarm threshold is set 50% above the clean filter pressure drop of 0.3 bar, providing adequate warning before the bypass valve opens and unfiltered fuel reaches the injectors. | subsystem, fuel-oil, sil-2, session-591
SUB-REQ-048 | When Day Tank level falls below the transfer initiation setpoint, the Fuel Transfer Pump SHALL automatically start and transfer fuel from the Bulk Storage Tank to the Day Tank within 30 minutes, with automatic stop on high level alarm and manual override capability from the EDG local control panel. | subsystem-requirements | Subsystem Requirements |  | Demonstration |  |  | Automatic transfer control ensures the Day Tank is replenished without operator intervention during sustained LOOP events when control room operator workload may be high. The 30-minute transfer time is derived from the Day Tank volume and transfer pump rated flow rate; this must be less than the 60-minute low-level alarm-to-starvation window to ensure reliable autonomous refill. | subsystem, fuel-oil, sil-2, session-591
SUB-REQ-049 | When Day Tank fuel level falls below the engine fuel inlet connection height, the Fuel Oil System SHALL generate a hardwired low-fuel trip signal to the EDG Instrumentation and Control System and the engine SHALL be shut down in a controlled manner to prevent injection pump dry-running damage. | subsystem-requirements | Subsystem Requirements |  | Test |  |  | SIL 2 safe-state requirement derived from SYS-REQ-010. Dry-running of the fuel injection pump for more than 30 seconds causes irreversible pump damage. A controlled shutdown (rather than sudden cutoff) is specified to allow the engine governor to reduce load before fuel cut-off, preventing electrical transients on the emergency bus. The trip signal follows the same hardwired, fail-safe discrete output architecture as the cooling loss trip. | subsystem, fuel-oil, sil-2, safety-trip, safe-state, session-591
SUB-REQ-050 | The Fuel Oil System bulk storage tank, day tank, pipework, and filter assembly SHALL comply with ATEX Directive 2014/34/EU Zone 2 classification, include double-walled bund containment capable of retaining 110% of the bulk tank volume, and be equipped with fuel leak detection with annunciation to the EDG control panel. | subsystem-requirements | Subsystem Requirements |  | Inspection |  |  | Diesel fuel storage at nuclear licensed sites is regulated under the ONR (Office for Nuclear Regulation) SA-EAF standard for fire and explosion prevention. ATEX Zone 2 classification is required because diesel vapour release in the EDG building during refuelling creates an intermittent flammable atmosphere. Double-walled bunding and leak detection are required by Environment Agency guidance on oil storage (PPG 2) to prevent fuel release into the nuclear site drainage system. | subsystem, fuel-oil, sil-2, safety, atex, session-591
SUB-REQ-051 | The Pre-Lube and Post-Lube Pump SHALL establish a minimum lubricating oil pressure of 1.5 bar at the engine main gallery within 20 seconds of receiving the pre-lubrication command, prior to the start air valve opening, to ensure all main and big-end bearings are wetted before cranking begins. | subsystem-requirements | Subsystem Requirements |  | Test |  |  | Dry start bearing damage is the primary engine wear failure mode for standby diesel engines. A minimum 1.5 bar gallery pressure confirmed before air start valve energisation ensures oil film thickness on all critical bearing surfaces; IEEE Std 387 and BS EN 12601 require pre-lubrication as a condition precedent to starting for standby EDGs.
SUB-REQ-052 | The Engine-Driven Lube Oil Pump SHALL maintain engine main gallery oil pressure within 3.5 bar to 5.5 bar at rated engine speed (750 rpm) and all operating temperatures within the normal range of 60°C to 100°C. | subsystem-requirements | Subsystem Requirements |  | Test |  |  | Sustained bearing film integrity requires oil pressure to exceed the hydrodynamic minimum across the full thermal operating range. The 3.5–5.5 bar band is derived from OEM bearing clearance analysis; pressures below 3.5 bar trigger thin-film conditions at operating temperature, and pressures above 5.5 bar risk seal extrusion on the crankshaft front and rear seals.
SUB-REQ-053 | The Lube Oil Cooler SHALL maintain engine lubricating oil outlet temperature within 80°C to 100°C at 100% rated engine load and maximum ambient design temperature of 40°C, using the closed-circuit engine jacket water as the cooling medium. | subsystem-requirements | Subsystem Requirements |  | Test |  |  | Oil viscosity falls non-linearly above 100°C; at temperatures exceeding 105°C, multigrade oil viscosity index is insufficient to prevent metal-to-metal contact in the turbocharger bearings. 80°C lower bound is set to prevent oil condensation and sludging during warm-up transients. Jacket water as cooling medium avoids the need for an independent cooler circuit, consistent with ARC-REQ-006.
SUB-REQ-054 | The Lube Oil Filter and Strainer SHALL maintain lubricating oil particle contamination downstream of the filter to ISO 4406 Class 17/15/12 or better throughout the EDG operational life, with an integral differential pressure indicator and high-differential-pressure alarm at 1.0 bar to alert operators before bypass valve opening. | subsystem-requirements | Subsystem Requirements |  | Test |  |  | Turbocharger bearing clearances on high-speed turbines are in the 20–30 micron range; contamination above ISO 4406 Class 17 introduces particulates large enough to score bearing surfaces. The 1.0 bar differential alarm provides advance warning at 50% of the bypass-open setpoint (2.0 bar), allowing a maintenance window without forced shutdown.
SUB-REQ-055 | The Pre-Lube and Post-Lube Pump SHALL continue post-shutdown lubrication circulation for a minimum of 10 minutes following EDG shutdown, maintaining oil gallery pressure above 0.8 bar to purge residual heat from the turbocharger bearing cartridge and prevent oil coking. | subsystem-requirements | Subsystem Requirements |  | Test |  |  | Turbocharger bearing cartridges retain thermal mass after shutdown; without continued lubrication, residual heat oxidises oil in the bearing clearances (oil coking), producing deposits that can block the oil feed bore on the next start. A 10-minute post-lube duration at 0.8 bar gallery pressure is consistent with OEM turbocharger specifications for medium-speed diesel engines at this power rating.
SUB-REQ-056 | When engine lubricating oil gallery pressure falls below 2.0 bar at any time during engine operation, the Engine Protection Relay Package SHALL initiate a hardwired engine trip within 500 ms, consistent with SUB-REQ-005, and the Lubrication and Bearing System SHALL shed all non-essential electrical consumers to prevent secondary damage. | subsystem-requirements | Subsystem Requirements |  | Test |  |  | 2.0 bar is the minimum hydrodynamic film-forming pressure at operating temperature for the main bearings; sustained operation below this threshold causes bearing wiping within 10–30 seconds. The 500 ms trip time limit is consistent with SUB-REQ-005 and provides a conservative margin above the estimated bearing failure time.
SUB-REQ-057 | The Automatic Voltage Regulator SHALL maintain the Synchronous Generator terminal voltage within ±1% of 6.6kV in steady-state at any load from 0% to 100% rated output current and power factor between 0.8 lagging and unity. | subsystem-requirements | Subsystem Requirements |  | Test |  |  | The 6.6kV emergency bus supplies Class 1E switchgear and motor starters with a declared operating voltage window of 6.6kV ±10%; maintaining AVR regulation to ±1% allocates a conservative tolerance budget that prevents motor starting problems even when the bus is at the low-voltage limit. Tighter regulation than the ±10% load-shedding protection window ensures stable operation under load sequencer step changes.
SUB-REQ-058 | The Automatic Voltage Regulator SHALL restore terminal voltage to within ±3% of 6.6kV within 1.5 seconds following a step load application of any individual safety load group connected by the load sequencer, without causing a generator protection trip. | subsystem-requirements | Subsystem Requirements |  | Test |  |  | Each load sequencer step applies a block load to the generator bus. The 1.5-second recovery window is derived from the motor starting immunity characteristic of downstream Class 1E motor starters; voltage dips exceeding 20% (i.e., below 5.28kV) lasting longer than 1.5 seconds can cause contactor dropout and loss of safety function. The AVR transient response specification directly supports SUB-REQ-010 load sequencer timing.
SUB-REQ-059 | The Generator Neutral Earthing Unit SHALL limit the earth fault current at the generator terminals to not more than 5 amperes (high-impedance earthing), using a resistor-loaded distribution transformer connected between the generator neutral point and earth, to restrict stator core damage during a phase-to-earth fault. | subsystem-requirements | Subsystem Requirements |  | Analysis |  |  | Unrestricted earth fault currents on medium-voltage generators cause stator core lamination burning that requires costly rewinding or core replacement. 5A high-impedance earthing is the standard approach for class I generators per IEC 60034-3; it limits core damage to the faulted slot only, allowing repair rather than replacement, and is consistent with the generator protection relay differential and earth-fault scheme in SUB-REQ-027.
SUB-REQ-060 | The Generator Cooling Fan SHALL start automatically upon engine rotation exceeding 50 rpm, maintain airflow through the stator winding and rotor end-turns throughout the operating period, and continue to rotate by inertia for not less than 5 minutes following engine shutdown to remove residual stator winding heat. | subsystem-requirements | Subsystem Requirements |  | Test |  |  | Stator winding insulation class H (maximum 180°C hotspot) requires continuous forced cooling during and immediately after rated-load operation. The 50 rpm start threshold ensures cooling airflow is established before excitation is applied; the 5-minute coasting period is derived from the thermal time constant of the stator winding insulation system at rated load, preventing insulation ageing by capping post-load hotspot temperature rise.
SUB-REQ-061 | The Automatic Voltage Regulator SHALL be classified as Class 1E I&C equipment per IEC 60780 and IEEE Std 603, and SHALL be qualified to operate across the seismic demand of the EDG site (0.5g peak spectral acceleration at 5 Hz) per IEEE Std 344, with at least one full operational test cycle performed under simulated seismic conditions. | subsystem-requirements | Subsystem Requirements |  | Inspection |  |  | The AVR is an active I&C function whose failure during a seismic event would deprive the site of AC power at the moment it is most needed (post-earthquake station blackout). IEEE Std 603 and IEC 60780 require Class 1E qualification for I&C elements that are credited in the safety case; IEEE Std 344 seismic qualification is mandated by the ONR ENSREG SSE design basis, consistent with SYS-REQ-009 and ARC-REQ-002.
SYS-REQ-001 | The Emergency Diesel Generator SHALL start and reach rated voltage (6.6kV ±10%) and rated frequency (50Hz ±2%) within 10 seconds of receiving a loss-of-offsite-power start signal. | system-requirements | System Requirements |  | Test | 100 |  | Derived from start-on-demand requirement and LOOP Response scenario. The 10-second target is the maximum time before safety loads lose cooling function. Exceeding 10 seconds risks fuel damage in a LOCA coincident with LOOP. H-001 (failure to start) is SIL 3. | system, sil-3, performance, session-570, idempotency:sys-start-time-570
SYS-REQ-002 | The Emergency Diesel Generator SHALL automatically start upon detection of bus undervoltage below 5.94kV (90% of nominal) without operator action, with LOOP detection completed within 100ms of grid voltage loss. | system-requirements | System Requirements |  | Test | 100 |  | Derived from operator alarm and LCO support needs. Automatic start eliminates operator response time from the safety function timeline. The 100ms detection window is standard for nuclear EDG undervoltage relays per IEEE 387 (IEEE Standard for the Design and Application of Diesel Generator Units for Class 1E Nuclear Power Generating Stations). H-001 SIL 3. | system, sil-3, safety, session-570, idempotency:sys-auto-start-570
SYS-REQ-003 | The Emergency Diesel Generator SHALL connect safety loads to the emergency bus via a priority-based load sequencer, with all safety loads energised within 60 seconds of EDG reaching rated output. | system-requirements | System Requirements |  | Test | 100 |  | Derived from operator display and LOOP Response scenario: loads sequenced in priority order — charging pumps first, then component cooling, then HVAC. 60-second window ensures reactor cooling is restored before fuel damage threshold. | system, sil-3, performance, session-570, idempotency:sys-load-sequence-570
SYS-REQ-004 | The Emergency Diesel Generator SHALL achieve a start-on-demand reliability of not less than 0.975 per demand, demonstrated through a minimum of 100 valid surveillance demands. | system-requirements | System Requirements |  | Analysis | 100 |  | Derived from licensee reliability target (STK-012). The 0.975 value comes from the probabilistic safety assessment; the 100-demand demonstration requirement provides 95% confidence that the true reliability meets the target. | system, reliability, session-570, idempotency:sys-start-reliability-570
SYS-REQ-005 | The Emergency Diesel Generator SHALL sustain continuous operation at rated load for a minimum of 24 hours with a mission reliability of not less than 0.999, without manual intervention beyond monitoring. | system-requirements | System Requirements |  | Test | 100 |  | Derived from licensee reliability target and Extended LOOP scenario: Day 2 of extended LOOP requires sustained EDG operation. The 24-hour mission defines the minimum design endurance before fuel replenishment or grid restoration. | system, reliability, session-570, idempotency:sys-mission-reliability-570
SYS-REQ-006 | The Emergency Diesel Generator SHALL maintain output voltage within 6.6kV ±10% and frequency within 50Hz ±2% under all load conditions from no-load to 110% rated load. | system-requirements | System Requirements |  | Test | 100 |  | Derived from operator display requirements. Safety loads (motors, transformers, UPS) require stable voltage and frequency. The ±10%/±2% tolerances are per IEEE 387 for Class 1E diesel generators. Voltage excursions outside these limits cause motor thermal damage or relay malfunction. | system, performance, session-570, idempotency:sys-output-quality-570
SYS-REQ-007 | The Emergency Diesel Generator installation SHALL comprise two independent, redundant trains (Train A and Train B) with no shared active components, such that a single failure in one train does not prevent the other from performing its safety function. | system-requirements | System Requirements |  | Analysis | 86 |  | Derived from ONR SAP compliance and community safety expectations. Single failure criterion is fundamental to nuclear safety system design per ONR SAP EKP.3. Common cause failure (H-007, SIL 4) is the highest-risk hazard identified. | system, sil-4, safety, session-570, idempotency:sys-redundancy-570
SYS-REQ-008 | The Emergency Diesel Generator fuel storage system SHALL hold a minimum 7-day fuel inventory at 100% rated load, with automatic transfer from bulk storage to engine day tank and continuous level monitoring. | system-requirements | System Requirements |  | Inspection | 100 |  | Derived from fuel constraint and Extended LOOP/SBO scenarios. The 7-day inventory covers the design basis LOOP duration plus margin for fuel delivery delays. H-005 (fuel exhaustion) is SIL 2. | system, sil-2, performance, session-570, idempotency:sys-fuel-capacity-570
SYS-REQ-009 | The Emergency Diesel Generator SHALL remain functional during and after a design basis earthquake of 0.2g peak ground acceleration (Seismic Category I), with no loss of ability to start and carry load. | system-requirements | System Requirements |  | Analysis | 100 |  | Derived from seismic environment constraint (STK-016) and H-008 (seismic damage, SIL 2). Seismic qualification per EUR requirements and IEC 60980 (Recommended practices for seismic qualification of electrical equipment of the safety system for nuclear generating stations). Post-earthquake operability is essential if LOOP coincides with seismic event. | system, sil-2, safety, session-570, idempotency:sys-seismic-570
SYS-REQ-010 | The Emergency Diesel Generator engine SHALL be protected by independent, hardwired trip circuits for overspeed (>115% rated), high coolant temperature, low lubricating oil pressure, and overcurrent, each capable of shutting down the engine within 2 seconds of trip setpoint. | system-requirements | System Requirements |  | Test | 86 |  | Derived from hazards H-003 (overspeed, SIL 2) and H-006 (cooling failure, SIL 2). Hardwired trips ensure protection even with digital control system failure. The 2-second trip time prevents engine mechanical damage at overspeed. | system, sil-2, safety, session-570, idempotency:sys-protection-570
SYS-REQ-011 | The Emergency Diesel Generator building SHALL incorporate automatic fire detection and suppression to extinguish diesel fuel fires without manual intervention, with inter-train fire barriers maintaining operability of the alternate EDG train. | system-requirements | System Requirements |  | Test | 71 |  | Derived from H-004 (fire in EDG building, SIL 2). Fire suppression must not damage the alternate EDG train. Train separation or fire barriers are needed to prevent common cause failure from fire propagation. | system, sil-2, safety, session-570, idempotency:sys-fire-protection-570, reqs-eng-session-583
SYS-REQ-012 | The Emergency Diesel Generator safety-related control and protection systems SHALL be isolated from non-safety networks, with safety trip functions implemented through hardwired circuits that cannot be defeated by cyber attack, per IEC 62645 (Nuclear power plants — Instrumentation, control and electrical power systems — Cybersecurity requirements). | system-requirements | System Requirements |  | Analysis | 86 |  | Derived from H-010 (cyber attack, SIL 3) and ONR SAP compliance. Air-gapped hardwired trip circuits provide defence-in-depth against cyber threats to digital control systems. | system, sil-3, safety, session-570, idempotency:sys-cyber-security-570
SYS-REQ-013 | The Emergency Diesel Generator SHALL support monthly surveillance testing via simulated LOOP signal initiation, a 2-hour run at 75% rated load, and automated parameter recording, without reducing availability of the alternate EDG train. | system-requirements | System Requirements |  | Demonstration | 71 |  | Derived from I&C calibration needs and Surveillance Test scenario: monthly test at 75% load for 2 hours with all parameters recorded. Test must not compromise the other train's availability. | system, testability, session-570, idempotency:sys-surveillance-570, reqs-eng-session-583
SYS-REQ-014 | When one EDG train is inoperable, the remaining train SHALL be capable of supplying 100% of the safety-critical electrical load, with the plant entering a Limiting Condition for Operation allowing no more than 72 hours for restoration before requiring controlled shutdown. | system-requirements | System Requirements |  | Analysis | 86 |  | Derived from shift supervisor LCO needs and EDG Failure to Start scenario: LCO 3.8.1 gives 72 hours. Each train must be sized for full safety load — no load shedding between trains. | system, sil-3, safety, session-570, idempotency:sys-single-train-570
SYS-REQ-015 | The Emergency Diesel Generator system SHALL provide a diverse alternate AC power source connection point, capable of accepting a mobile diesel generator of at least 50% safety load capacity within 4 hours of station blackout declaration. | system-requirements | System Requirements |  | Demonstration | 86 |  | Derived from H-007 (common cause failure, SIL 4) and Station Blackout scenario: mobile generator connected after 4.5 hours. The 4-hour target aligns with DC battery capacity and provides margin before battery exhaustion. | system, sil-4, safety, session-570, idempotency:sys-diverse-ac-570
VER-REQ-001 | The Diesel Engine Assembly cold-start acceptance test SHALL confirm self-sustaining rotation within 3 seconds of start signal when tested from -10°C ambient with the starting air system pre-charged to 25 bar. | verification-requirements | Verification Requirements |  | Test | 100 |  | Cold start at -10°C is the worst-case scenario for start time per STK-REQ-017; if the engine meets the 3-second criterion at minimum temperature it will meet it at all higher temperatures. The test confirms fuel injection system and compression pressure are sufficient for cold combustion. Procedure: record time via exhaust thermocouple response and starter air valve closure. | verification, diesel-engine-assembly, session-571, idempotency:ver-sub001-cold-start-571, reqs-eng-session-577
VER-REQ-002 | The Engine Protection Relay Package functional test SHALL confirm each trip relay (overspeed at 865 rpm, high coolant temperature at 91°C, low oil pressure at 1.9 bar) actuates within 2 seconds with the digital control system de-energised. | verification-requirements | Verification Requirements |  | Test | 86 |  | Testing with the digital control system de-energised confirms fail-safe operation of the hardwired protection as required by ARC-REQ-002 and IEC 61513. The 2-second criterion is derived from the 5-second engine standstill requirement (VER-REQ-003) leaving margin for fuel rack response. Each channel must be tested independently to confirm there is no shared-mode defeat path. | verification, diesel-engine-assembly, sil-3, safety-trip, session-571, idempotency:ver-sub-protection-trips-571, reqs-eng-session-577
VER-REQ-003 | The Diesel Engine Assembly protection trip test SHALL confirm engine standstill (crankshaft speed below 5 rpm) within 5 seconds of manual trip signal for each of the three protection relay channels at 50% rated load. | verification-requirements | Verification Requirements |  | Test | 100 |  | Testing at 50% load represents a conservative loaded condition without risk of overloading the test power system. Five seconds to standstill bounds the fuel injection system response time and confirms the mechanical trip train integrity. Each of the three channels is tested in independent runs to eliminate compensating failure detection. | verification, diesel-engine-assembly, sil-3, safe-state, session-571, idempotency:ver-sub009-safe-state-571, reqs-eng-session-577
VER-REQ-004 | The Fuel Injection System interface acceptance test SHALL confirm steady-state fuel feed pressure at the injection pump inlet is 3.0–5.0 bar and fuel cleanliness is ISO 4406 class 18/16/13 or cleaner at rated engine load. | verification-requirements | Verification Requirements |  | Test | 100 |  | The 3.0–5.0 bar pressure range is the OEM injection pump inlet specification; exceedance causes injector spray pattern degradation and sub-band triggers pump cavitation. ISO 4406 class 18/16/13 is the OEM-specified cleanliness limit above which injection nozzle wear rate increases non-linearly. Test at rated load produces worst-case fuel flow and thermal state. | verification, diesel-engine-assembly, session-571, idempotency:ver-ifc008-fuel-supply-571, reqs-eng-session-577
VER-REQ-005 | The Starting Air System interface test SHALL confirm air start distributor inlet pressure of 25–30 bar at start signal initiation and engine cranking speed reaching 120 rpm within 1.5 seconds, repeated at -10°C ambient. | verification-requirements | Verification Requirements |  | Test | 100 |  | The 25–30 bar inlet pressure range brackets the OEM cranking torque requirement for reliable first-cycle ignition. Achieving 120 rpm within 1.5 seconds confirms the air volume and flow rate are sufficient for the mechanical compression ratio of the engine. Repeating at -10°C validates the system under the worst-case viscosity and thermal conditions per STK-REQ-017. | verification, diesel-engine-assembly, sil-3, session-571, idempotency:ver-ifc011-start-air-571, reqs-eng-session-577
VER-REQ-006 | The end-to-end EDG start chain acceptance test SHALL confirm bus undervoltage detection within 100 ms, rated voltage and frequency within 10 seconds, and all safety loads connected within 60 seconds of a LOOP signal below 5.94 kV under 100% rated load. | verification-requirements | Verification Requirements |  | Test | 86 |  | This integrated test verifies the complete start chain: LOOP detection (SYS-REQ-002), engine start (SUB-REQ-001), rated output (SYS-REQ-001), and load sequencing (SYS-REQ-003). Testing under 100% rated load step represents the worst-case voltage dip at breaker close. Data sampled at 100 Hz from LOOP detection to full load connection provides the evidence chain for ONR surveillance records. | verification, integration, sil-3, session-571, idempotency:ver-integration-edg-start-chain-571, reqs-eng-session-577
VER-REQ-007 | The Diesel Engine Assembly 24-hour endurance test SHALL confirm continuous operation at rated output with speed variation not exceeding 750 rpm ±7.5 rpm at all measurement points throughout the test duration. | verification-requirements | Verification Requirements |  | Test | 100 |  | The 24-hour duration demonstrates suitability for extended station blackout events per IEEE 387 and STK-REQ-005. Speed variation ±1% of synchronous speed (750 ±7.5 rpm) is the IEC 60034 governing limit for generator frequency stability; exceedance would cause protective relay operations. Speed is recorded at 1-second intervals at 0h, 1h, 4h, 8h, 16h, and 24h to detect drift and degradation. | session-572, verification, diesel-engine-assembly, idempotency:ver-sub002-003-endurance-572, reqs-eng-session-577
VER-REQ-008 | The EDG automatic start acceptance test SHALL confirm LOOP detection within 200 ms and bus voltage rising to 6.6 kV ±10% within 10 seconds of a simulated undervoltage signal at 5.80 kV, verified in three consecutive tests from cold standby. | verification-requirements | Verification Requirements |  | Test | 86 |  | Three consecutive tests from cold standby demonstrate the statistical reliability of the start chain rather than a single-shot result. The 5.80 kV stimulus (below the 5.94 kV threshold) represents the worst-case detection-margin operating point. Ten-second voltage rise aligns with SYS-REQ-001 and IEEE 387 acceptance criteria for nuclear emergency diesel generators. | session-572, verification, loop-detection, idempotency:ver-ifc001-002-loop-572, reqs-eng-session-577
VER-REQ-009 | The Emergency Diesel Generator seismic qualification SHALL demonstrate by analysis per IEEE 344 that all safety-related mounting interfaces maintain structural integrity and functionality at Seismic Category I (0.3g horizontal, 0.2g vertical ZPA). | verification-requirements | Verification Requirements |  | Analysis | 100 |  | IEEE 344 (IEEE Recommended Practice for Seismic Qualification of Class 1E Equipment for Nuclear Power Generating Stations) is the mandatory qualification standard for safety-related equipment. Analysis using the Original Design Specification static seismic loads is the primary method; shake table testing per IEC 60980 is the fallback if analysis is insufficient. Qualification covers engine cradle welds, generator stator support, and control panel anchors. | session-572, verification, seismic, idempotency:ver-sub008-seismic-572, reqs-eng-session-577
VER-REQ-010 | The Load Sequencer acceptance test SHALL confirm the first priority load group connects within 1 second of generator breaker closure and total safety load restoration completes within 10 seconds with generator voltage remaining within 6.6 kV ±10%. | verification-requirements | Verification Requirements |  | Test | 86 |  | The 1-second first-group connection criterion limits the dip in essential bus voltage to within generator transient recovery limits. The 10-second total restoration window aligns with SYS-REQ-003 load connection requirement. The 500 ms minimum interval between groups is the OEM-specified generator transient recovery time to prevent cumulative voltage collapse. Test uses a resistive load bank per priority group at 10 ms timestamp resolution. | session-572, verification, switchgear-load-sequencer, idempotency:ver-sub010-load-seq-572, reqs-eng-session-577
VER-REQ-011 | The Diesel Fuel Injection System acceptance test SHALL confirm fuel delivery metering by measuring cylinder-to-cylinder fuel quantity variation using a calibrated combustion analyser at steady-state rated load, achieving ≤±3% of mean fuel quantity per injection event per SUB-REQ-007. | verification-requirements | Verification Requirements |  | Test | 86 |  | SUB-REQ-007 mandates ±3% cylinder-to-cylinder fuel variation to prevent thermal overload; this VER entry provides the specific test procedure — combustion analyser measurement during the monthly surveillance test (SYS-REQ-013). Without an explicit test, injection pump calibration drift could exceed the limit between overhaul intervals, increasing crankshaft fatigue and catastrophic failure risk (hazard H-001). | session-580, qc, verification, diesel-engine-assembly, idempotency:ver-fuel-injection-metering-580
VER-REQ-012 | The Fuel Oil System volume acceptance test SHALL confirm minimum usable fuel inventory by physical measurement of day tank and bulk storage tank levels under operating conditions, verifying ≥7,000 litres per EDG train with fuel meeting CIMAC Class DM specification per SUB-REQ-011. | verification-requirements | Verification Requirements |  | Inspection | 86 |  | SUB-REQ-011 mandates a 7,000-litre minimum inventory for 7-day mission duration. Inspection of tank contents and fuel quality certificate ensures the 7-day SBO mission (STK-REQ-005, SYS-REQ-008) can be sustained. Fuel quality verification (CIMAC DM) prevents injection system contamination damage during extended operation when no commercial resupply is possible. | session-580, qc, verification, fuel-oil-system, idempotency:ver-fuel-oil-inventory-580
VER-REQ-013 | The Ultimate Heat Sink cooling water interface acceptance test SHALL confirm minimum flow of 150 m³/h at ≤30°C inlet temperature under rated load conditions using calibrated flow meters, verifying IFC-REQ-003 compliance and confirming jacket water outlet temperature remains below 88°C thermostat setpoint. | verification-requirements | Verification Requirements |  | Test | 86 |  | IFC-REQ-003 defines the cooling water flow and temperature requirement at the EDG/UHS boundary. Testing under rated load conditions is required to confirm heat exchanger performance prior to nuclear plant commissioning — failure to achieve adequate flow would cause engine overtemperature and forced shutdown of the EDG, defeating the safety function during accident conditions. | session-580, qc, verification, cooling, idempotency:ver-uhs-cooling-interface-580
VER-REQ-014 | The Emergency Diesel Generator MCR interface functional test SHALL verify that all specified analogue and digital EDG operating parameters display correctly at the MCR console, all abnormal condition alarms actuate within 2 seconds of simulated fault injection, and manual start/stop commands are executed within 5 seconds, over the qualified Class 1E cabling per IFC-REQ-005. | verification-requirements | Verification Requirements |  | Test | 86 |  | IFC-REQ-005 specifies the MCR interface signals required for operator monitoring and control. Functional testing of all alarm and command channels is required by ONR Safety Assessment Principles — the operator must be able to diagnose and respond to EDG abnormalities from the MCR during a design basis accident. Without testing, Class 1E cabling faults may prevent alarms from reaching the operator at the critical moment. | session-580, qc, verification, mcr-interface, idempotency:ver-mcr-interface-580
VER-REQ-015 | The Fuel Supply infrastructure interface inspection SHALL verify the fuel fill connection, overfill protection activation at 95% tank capacity, and automatic day tank level management by confirming minimum 2-hour fuel reserve is maintained during simulated bulk transfer pump failure per IFC-REQ-006. | verification-requirements | Verification Requirements |  | Demonstration | 86 |  | IFC-REQ-006 defines overfill protection and day tank management at the external fuel supply boundary. Demonstration of overfill cutoff prevents environmental release of diesel fuel (a licensable offence at a nuclear site). The 2-hour day tank reserve demonstration confirms EDG resilience to a short-duration bulk transfer pump failure without manual intervention, which is the credited operator action in the fuel replenishment scenario. | session-580, qc, verification, fuel-supply-interface, idempotency:ver-fuel-supply-interface-580
VER-REQ-016 | The DC Battery System interface acceptance test SHALL verify 125VDC Class 1E control power availability to EDG instrumentation and control equipment with battery voltage maintained within ±2% of nominal during simulated LOOP conditions, and confirm battery charger re-energisation from EDG output bus within 30 seconds of EDG starting per IFC-REQ-007. | verification-requirements | Verification Requirements |  | Test | 86 |  | IFC-REQ-007 specifies the DC power interface critical for EDG control system function and subsequent restart capability. The battery charger re-energisation test validates the feedback loop (EDG powers charger → charger maintains battery → battery enables subsequent starts) that must function during extended LOOP events. Voltage tolerance of ±2% ensures relay pick-up voltages remain within manufacturer specification throughout the demand event. | session-580, qc, verification, dc-battery-interface, idempotency:ver-dc-battery-interface-580
VER-REQ-017 | Verify SUB-REQ-014: Starting Air System factory acceptance test SHALL measure actual air receiver bank pressure using calibrated gauges after full charge, confirm minimum 25 bar and maximum 30 bar on both banks, then perform three consecutive simulated start blows and confirm post-test pressure on each bank remains above 20 bar. | verification-requirements | Verification Requirements |  | Test | 86 |  | Direct pressure measurement confirms receiver sizing and charge pressure setpoints. Three-blow test confirms capacity margin for the minimum required start attempts without recharging. | verification, starting-air-system, session-581, idempotency:ver-sub014-sas-receivers-581
VER-REQ-018 | Verify SUB-REQ-019: I&C LOOP detection acceptance test SHALL apply a simulated bus undervoltage to the Qualified I/O Module input, confirm undervoltage flag set within 100 ms by data logging at 1 ms resolution, and confirm air start command hardwired output energised within 200 ms of input application. Test shall be repeated five times with no failures. | verification-requirements | Verification Requirements |  | Test | 86 |  | Timing verification at 1 ms resolution is necessary to demonstrate 100 ms detection budget compliance. Five repetitions provide statistical confidence that the timing is not marginal. Pass criterion is 100 percent compliance — a single timing violation fails the test. | verification, ic-system, sil-3, session-581, idempotency:ver-sub019-ic-loop-detection-581
VER-REQ-019 | Verify SUB-REQ-020: Engine and Generator Protection Logic functional test SHALL inject simulated overspeed, low oil pressure, and high coolant temperature signals at trip setpoints and confirm de-energise-to-trip relay output achieved within 200 ms of signal injection, measured by oscilloscope at 0.1 ms resolution. Each trip function shall be tested individually and in combination. | verification-requirements | Verification Requirements |  | Test | 86 |  | Individual and combination testing confirms that no single trip function can be masked by another and that the combined protection logic does not introduce additional latency when multiple alarms are active simultaneously. | verification, ic-system, sil-3, safety-trip, session-581, idempotency:ver-sub020-ic-protection-trip-581
VER-REQ-020 | Verify SUB-REQ-023: I&C self-diagnostic safe-state test SHALL inject a simulated SIL 3 logic self-fault and confirm de-energise-to-trip output within 500 ms, control room fault alarm within 5 seconds, and last-good HMI status data preserved. Pass criterion: all three conditions met in five consecutive fault injections. | verification-requirements | Verification Requirements |  | Test | 86 |  | Safe-state transition testing is mandatory under IEC 61508 SIL 3 to demonstrate the safe failure fraction target. Five repetitions confirm reproducibility. HMI data preservation is verified separately to confirm operators are not left without status during a critical event. | verification, ic-system, sil-3, safe-state, session-581, idempotency:ver-sub023-ic-safe-state-581
VER-REQ-021 | Verify IFC-REQ-014: Integration test SHALL energise the I&C start command hardwired output to the SAS air start valve, confirm solenoid energisation by discrete feedback within 200 ms of simulated LOOP signal, and verify 125VDC Class 1E power rail maintained throughout the test cycle under simulated loss of normal AC supply. | verification-requirements | Verification Requirements |  | Test | 86 |  | Integration test at the physical interface confirms hardwired signal routing, voltage level, and timing as actually installed — bench-level component tests cannot confirm cable routing or terminal block integrity. | verification, interface, starting-air-system, ic-system, session-581, idempotency:ver-ifc014-ic-sas-start-581
VER-REQ-022 | Verify IFC-REQ-015: SAS pressure monitoring interface test SHALL confirm 4-20 mA signal range maps correctly to 0-35 bar at the I&C input, scan interval at 1 Hz or faster, and hardwired alarm contacts close within 5 seconds of simulated low-pressure fault injection on each bank independently. | verification-requirements | Verification Requirements |  | Test | 71 |  | Separate verification of the analogue and discrete paths confirms both are functional simultaneously — a common failure mode is a broken hardwired contact that is masked by the healthy analogue signal. | verification, interface, starting-air-system, ic-system, session-581, idempotency:ver-ifc015-sas-pressure-monitor-581
VER-REQ-023 | Verify SUB-REQ-024: The Bus Undervoltage Sensing Relay factory acceptance test SHALL inject a simulated 4.5kV signal (sustained for 250ms) on each of the three VT inputs independently and confirm automatic start output active within 200ms; SHALL inject a transient dip to 4.5kV lasting only 150ms and confirm no start output; SHALL disable one VT input and confirm two-out-of-three voting still produces start output at 4.5kV sustained 250ms. | verification-requirements | Verification Requirements |  | Test | 86 |  | Three test scenarios verify the three distinct aspects of SUB-REQ-024: timing, transient rejection, and voting logic. All three must pass for the requirement to be verified; failure of any one scenario is a compliance failure against the safety function. | verification, electrical-switchgear-and-load-sequencer, sil-3, session-582, idempotency:ver-sub024-buvr-582
VER-REQ-024 | Verify SUB-REQ-026: The Synchronising Check Relay acceptance test SHALL inject voltage, frequency, and phase angle combinations at boundary conditions (voltage ±10% nominal, frequency ±0.5Hz, phase ±10 degrees) and verify close permission asserts only within the window; SHALL reduce bus voltage to 10% nominal (0.66kV) sustained for 600ms and verify dead-bus close permission asserts without frequency or phase angle check within 500ms. | verification-requirements | Verification Requirements |  | Test | 86 |  | Boundary condition testing of each synchronising window independently confirms the requirement is met at the most challenging operating points. The dead-bus override test uses 10% nominal (half the 20% threshold) to confirm reliable operation; testing at exactly 20% is insufficient because relay operating band tolerances could cause a false pass. | verification, electrical-switchgear-and-load-sequencer, sil-3, session-582, idempotency:ver-sub026-sync-check-582
VER-REQ-025 | Verify IFC-REQ-016: Integration test SHALL measure cable loop resistance on the BUVR-to-GCB start circuit at commissioning and confirm it is below 20 ohms; SHALL inject open-circuit fault on the start signal cable and confirm the EDG automatic start sequence initiates (failsafe open-circuit equals start demand); SHALL verify cable routing segregation from non-Class 1E cables by visual inspection against cable tray drawings. | verification-requirements | Verification Requirements |  | Test | 86 |  | Three verification methods address the three distinct aspects of IFC-REQ-016: cable resistance (continuity), failsafe logic (functional), and segregation (inspection). Resistance must be measured at commissioning not just at factory because field cable lengths are not fixed at design. Segregation requires visual inspection against as-built drawings since it cannot be functionally tested. | verification, electrical-switchgear-and-load-sequencer, sil-3, session-582, idempotency:ver-ifc016-buvr-gcb-582
VER-REQ-026 | Verify IFC-REQ-018: The trip circuit commissioning test SHALL measure total trip circuit resistance and confirm it does not exceed 10 ohms; SHALL apply an open-circuit fault at the protection relay trip contact and verify an MCR alarm appears within 5 seconds; SHALL inject a simulated protection trip and measure GCB trip time from protection relay output to GCB open confirming it is within 100ms at nominal 125VDC and 95VDC. | verification-requirements | Verification Requirements |  | Test | 86 |  | Trip circuit resistance and timing must both be measured at commissioning because field cabling resistance is not determined until installation. The supervision alarm test verifies the wiring integrity monitoring function independently. Testing at 95VDC (minimum battery voltage) is required by IEC 61508 SIL 3 hardware validation to demonstrate worst-case operation under degraded power supply conditions. | verification, electrical-switchgear-and-load-sequencer, sil-3, session-582, idempotency:ver-ifc018-geprp-gcb-trip-582
VER-REQ-027 | Verify IFC-REQ-017: The Synchronising Check Relay to GCB close-permission interface acceptance test SHALL confirm close permission asserts only when both voltage and frequency are simultaneously within window (boundary combination testing with 9 combinations covering all quadrant boundaries); SHALL inject an anti-pumping test with two consecutive close commands and confirm only one close attempt completes; SHALL withdraw synchronising permission mid-operation and confirm GCB close does not complete. | verification-requirements | Verification Requirements |  | Test | 86 |  | Nine boundary-combination tests are the minimum to verify the AND logic of the three synchronising conditions without testing all permutations. Anti-pumping and permission-withdrawal tests verify the two protection mechanisms specified in IFC-REQ-017 that cannot be inferred from steady-state tests alone. | verification, electrical-switchgear-and-load-sequencer, sil-3, session-582, idempotency:ver-ifc017-scr-gcb-close-582
VER-REQ-028 | The Generator Circuit Breaker close-time acceptance test SHALL confirm GCB closure onto the 6.6 kV emergency bus within 100 ms of receiving a close command, measured from control relay energisation to primary contact make, under rated bus voltage with simulated safety load. | verification-requirements | Verification Requirements |  | Test |  |  | SUB-REQ-025 specifies GCB close time of 100 ms; safety-critical because post-LOOP bus restoration depends on GCB closing before load sequencing begins, and a slow GCB extends bus dead time beyond the 10-second SYS-REQ-001 budget. MoP basis: IEC 62271-100 (High-voltage alternating-current circuit-breakers) defines close-time as the interval from close-coil energisation to primary contact make; 100 ms is within the Class C2 mechanical operating time envelope for 6.6 kV vacuum circuit-breakers. | idempotency:ver-req-sub025-gcb-583, reqs-eng-session-583
VER-REQ-029 | The Generator Electrical Protection Relay Package functional test SHALL inject a simulated differential current exceeding 5% of rated CT primary current and confirm trip relay operation within 50 ms, with secondary injection confirming correct phase angle discrimination. | verification-requirements | Verification Requirements |  | Test |  |  | SUB-REQ-027 requires 87G differential protection with a pickup threshold; this test confirms relay operation within specified timing at the threshold current, the minimum demonstration needed for IEC 60255-151 (Measuring relays and protection equipment) compliance on a UK nuclear site. | idempotency:ver-req-sub027-gen-87g-583, reqs-eng-session-583
VER-REQ-030 | The Generator Electrical Protection Relay Package trip circuit test SHALL confirm that a protection trip condition causes GCB trip coil energisation within 60 ms and generator field de-excitation within 200 ms, measured from initial fault signal to generator terminal voltage below 10% rated. | verification-requirements | Verification Requirements |  | Test |  |  | SUB-REQ-028 specifies the generator de-energise path on protection trip; timing from fault to terminal voltage collapse determines the duration of fault current fed into any bus fault, so the 60ms/200ms thresholds protect against damage to safety loads on the 6.6kV bus. MoP basis: IEC 60255-151 (Measuring relays and protection equipment — functional requirements for over/undercurrent protection) requires relay operate time measurement within ±5% of stated value; 60 ms trip coil energisation and 200 ms field collapse are derived from the generator manufacturer's demagnetisation time constant (typically 100–300 ms for safety-grade machines). | idempotency:ver-req-sub028-gen-trip-583, reqs-eng-session-583
VER-REQ-031 | The EDG I&C Qualified I/O Module Assembly isolation qualification test SHALL apply 1.5 kV RMS AC voltage for 60 seconds between each safety-classified circuit and non-Class-1E circuit, confirming leakage current below 1 mA, and SHALL repeat after a simulated 0.3g PGA seismic table test per IEEE 344. | verification-requirements | Verification Requirements |  | Test |  |  | SUB-REQ-021 requires 1.5 kV RMS Class 1E isolation maintained post-seismic; IEC 60780 (Nuclear power plants — Electrical equipment of the safety system) and IEC 60255 (Measuring relays and protection equipment) both specify dielectric withstand at 1.5 kV as the acceptance threshold for Class 1E signal isolation. The post-seismic repeat confirms that the seismic event has not degraded the isolation barrier — a critical pass for the common-cause failure safety argument. | idempotency:ver-req-sub021-io-isolation-583, reqs-eng-session-583
VER-REQ-032 | The Starting Air System Air Compressor and Recharge Unit recharge acceptance test SHALL start both compressors with both Air Receiver Banks at 20 bar and confirm pressure of 30 bar is reached within 30 minutes, measured at the receiver outlets, with the compressors at ambient temperature at test start. | verification-requirements | Verification Requirements |  | Test |  |  | SUB-REQ-016 specifies a 30-bar/30-minute recharge criterion following a three-start sequence. Post-start recharge capability is safety-critical because a second emergency demand within 30 minutes requires a full-pressure air system. The acceptance test must start from the worst-case 20-bar post-start low to confirm the compressor capacity under design conditions, not just steady-state operation. | session-585, qc, starting-air-system, idempotency:ver-sub016-recharge-585
VER-REQ-033 | The Starting Air System Moisture Separator and Drain System commissioning inspection SHALL measure compressed air dewpoint at each Air Receiver Bank outlet using a calibrated chilled-mirror hygrometer after 24 hours of system operation, confirming dewpoint at or below minus 40°C at atmospheric pressure. | verification-requirements | Verification Requirements |  | Inspection |  |  | SUB-REQ-017 requires dewpoint ≤ −40°C to prevent ice formation in distribution manifolds and air-start valves during cold ambient conditions (design minimum: −15°C). Chilled-mirror hygrometry is the accepted reference measurement method per ISO 8573-1 (Compressed air quality). The 24-hour steady-state operation period ensures the separator and auto-drain cycle are active and the air system has purged residual commissioning moisture before measurement. | session-585, qc, starting-air-system, idempotency:ver-sub017-dewpoint-585
VER-REQ-034 | The Starting Air System pressure monitoring functional test SHALL verify: (a) with receiver pressure reduced to 27 bar, a control room annunciation appears within 5 seconds; (b) with pressure reduced to 22 bar, the EDG I&C inhibits further start attempts from that bank; (c) with pressure restored above 25 bar, the inhibit clears and start attempts are permitted. | verification-requirements | Verification Requirements |  | Test |  |  | SUB-REQ-018 requires two threshold-triggered actions (27-bar alarm, 22-bar inhibit) that protect the starting air system from being depleted below the minimum single-start pressure. Testing each threshold in sequence verifies both the alarm function and the inhibit logic, and the restore test confirms the inhibit is not latching beyond design intent — all three checks are required to verify the complete requirement. | session-585, qc, starting-air-system, idempotency:ver-sub018-pressure-alarm-585
VER-REQ-035 | The EDG I&C Plant Communication Gateway isolation verification test SHALL confirm unidirectionality by: (a) transmitting a data packet from the safety-classified I&C to the MCR network side; (b) injecting an arbitrary signal on the MCR network side and confirming no signal is detectable on the safety-classified I&C side using a calibrated oscilloscope with 1mV sensitivity. | verification-requirements | Verification Requirements |  | Test |  |  | SUB-REQ-022 requires a data diode with no return path to safety-classified I&C. A passive electrical injection test from the normal side — not just a software-level attempt — is required because the safety case must exclude hardware-level coupled pathways. The 1mV sensitivity threshold is taken from IEC 62645 (Nuclear power plants — I&C systems — Requirements for security programmes) acceptance criteria for isolation verification. | session-585, qc, ic-system, cybersecurity, idempotency:ver-sub022-data-diode-585
VER-REQ-036 | The EDG Building fire protection commissioning inspection SHALL confirm: (a) automatic suppression system actuates on test signal within 5 seconds of detector activation and achieves gas concentration per BS EN 15004 within 30 seconds; (b) two-hour fire-rated barrier is confirmed by documentation review of BS 476 Part 22 certification for all penetrations, doors, and cable transits between Train A and Train B rooms. | verification-requirements | Verification Requirements |  | Inspection |  |  | SUB-REQ-029 specifies a 30-second suppression criterion and a two-hour fire barrier. The inspection combines a functional actuation test (verifying the 30-second time criterion on the actual installed system) with documentary evidence review for the barrier certification, since the two-hour rating is established by material qualification test certificates, not an in-situ burndown test. | session-585, qc, edg-building, fire-protection, idempotency:ver-sub029-fire-585
VER-REQ-037 | Verify IFC-REQ-019: During commissioning, measure combustion air velocity at three points across the engine intake plenum cross-section using a calibrated anemometer at rated fan speed. PASS if all readings are at or below 8 m/s and filter differential pressure is within the range specified for ISO 16890 ePM1 55% filters. | verification-requirements | Verification Requirements |  | Test |  |  | Integration test verifying intake air velocity and filter compliance at the engine air intake plenum. Velocity at three points covers the cross-section to detect non-uniform flow distribution that could cause localised engine intake starvation. | verification, edg-building, hvac, session-586, idempotency:ver-ifc019-hvac-air-v2-586
VER-REQ-038 | Verify IFC-REQ-020: During integrated fire protection commissioning, simulate a confirmed fire detection signal and measure elapsed time from signal generation to full damper closure and fan de-energisation. PASS if both conditions are achieved within 5 seconds on all three test repetitions; any single-run time exceeding 7 seconds is a fail. | verification-requirements | Verification Requirements |  | Test |  |  | End-to-end functional test of the fire detection to HVAC isolation hardwired interface. Three repetitions detect intermittent relay faults or damper actuator stiction. The 7-second single-run limit provides margin for relay pick-up jitter while ensuring the mean meets the 5-second requirement threshold. | verification, edg-building, fire, hvac, session-586, idempotency:ver-ifc020-fire-hvac-v2-586
VER-REQ-039 | Verify IFC-REQ-021: During commissioning inspection, trace the bunded drain path from each Fuel Oil System component (day tank, fill connections, transfer pump, fuel filter) to the sump. PASS if every fuel-wetted component has a continuous bunded path to the sump with no uncontained intermediate drip points, and sump net capacity (measured by survey) equals or exceeds 4,400 litres. | verification-requirements | Verification Requirements |  | Inspection |  |  | Bunded drain path integrity cannot be verified by functional test without deliberate fuel release; inspection of the physical drain routing during commissioning is the appropriate verification method. Sump capacity is verified by dimensional survey against the design drawing, which is both more accurate and safer than a wet test with 4,000L of diesel fuel in a nuclear facility. | verification, edg-building, flood, fuel, session-586, idempotency:ver-ifc021-drain-fuel-586
VER-REQ-040 | Verify SUB-REQ-030: Perform seismic analysis of the Category 1 Building Structure in accordance with BS EN 1998-1 (Eurocode 8: Design of Structures for Earthquake Resistance) using the site-specific design basis spectrum at 0.2g PGA. PASS if maximum computed deflection at any equipment anchor point is at or below 10mm under the design basis loading combination. | verification-requirements | Verification Requirements |  | Analysis |  |  | Full-scale seismic testing of a reinforced concrete EDG building is not practicable; analysis to Eurocode 8 is the standard method accepted by ONR for demonstrating seismic Category I structural integrity. The analysis must use the site-specific design response spectrum, not a generic spectrum, to account for local soil conditions at the nuclear site. | verification, edg-building, seismic, sil-2, session-586, idempotency:ver-sub030-seismic-586
VER-REQ-041 | Verify EDG Building and Support Systems integration: During EDG system integrated test, initiate EDG start from simulated LOOP signal and verify simultaneously: (a) HVAC fans reach rated airflow within 30 seconds; (b) exhaust backpressure does not exceed 50 mbar at 100% rated load; (c) sump high-level alarm is operational; (d) fire detection to HVAC damper isolation operates within 5 seconds on test signal. PASS if all four criteria are met in a single test run at rated load. | verification-requirements | Verification Requirements |  | Test |  |  | Integration test exercises all EDG Building and Support Systems components simultaneously as the EDG loads to rated output. Individual component tests cannot detect integration conflicts such as HVAC fan vibration affecting fire detector sensitivity, or exhaust system resonance under combined HVAC and engine load. This test validates that all building sub-functions are compatible at full load. | verification, edg-building, integration, session-586, idempotency:ver-building-integration-586
VER-REQ-042 | Verify EDG Building inter-train separation: During pre-operational inspection, measure the clear distance between Train A and Train B building compartments at the nearest point and confirm not less than 600 mm. Verify that no penetrations, shared ducting, or cable routes cross the separation barrier without fire stops. PASS if measured separation is ≥600 mm and no unprotected penetrations are found. | verification-requirements | Verification Requirements |  | Inspection |  |  | Physical separation between trains is a passive, permanent attribute of the building structure that can only be verified by dimensional inspection; functional testing cannot confirm structural independence. The 600 mm minimum from SUB-REQ-031 is derived from nuclear separation distance requirements in BS EN 61513. | verification, edg-building, seismic, session-589, qc, idempotency:ver-building-separation-589, idempotency:ver-building-separation-589
VER-REQ-043 | Verify Ventilation and Combustion Air System airflow performance: With the EDG running at 100% rated load, measure total combustion air mass flow at the engine air intake manifold using calibrated anemometry. PASS criterion: measured airflow ≥0.55 kg/s. Perform at ambient temperatures of 10°C, 25°C, and 40°C to verify margin across the design envelope. | verification-requirements | Verification Requirements |  | Test |  |  | Combustion air supply is a direct determinant of engine power output and fuel combustion efficiency; insufficient airflow at rated load causes manifold pressure drop, elevated exhaust temperature, and power output shortfall. Testing at three ambient temperatures confirms that the passive inlet design in SUB-REQ-032 delivers the required flow across the full UK operating temperature range. | verification, edg-building, hvac, session-589, qc, idempotency:ver-combustion-air-flow-589, idempotency:ver-combustion-air-flow-589
VER-REQ-044 | Verify EDG Building structural breach detection and automatic trip: With EDG in running state, simulate a structural breach detection signal via test input to the structural monitoring system. Verify that the EDG automatic trip signal is generated and the engine initiates shutdown within 5 seconds of simulated breach detection. PASS if shutdown sequence initiates within 5 seconds and main control room alarm is annunciated within 60 seconds. | verification-requirements | Verification Requirements |  | Test |  |  | Structural breach detection and automatic trip is a safety function preventing EDG operation in a structurally compromised enclosure (e.g., post-seismic event with building damage); the trip must be fast enough to prevent additional secondary damage while the main control room alarm allows operators to assess and respond. Functional test using simulated input per IEC 61513 (Nuclear power plants — Instrumentation and control important to safety — General requirements for systems) verification requirements is necessary to confirm the monitoring-to-trip signal chain without inducing actual structural damage. | verification, edg-building, seismic, session-589, qc, idempotency:ver-building-breach-trip-589, idempotency:ver-building-breach-trip-589
VER-REQ-047 | Verify IFC-REQ-022: Coolant Circulation Pump performance test at 25%, 50%, 75%, 100%, and 110% rated engine load. Pass criterion: flow ≥150 L/min, delivery pressure ≥0.8 bar gauge, suction pressure ≥0.2 bar at each load point. Measured by calibrated flow meter and pressure transducers at pump inlet and outlet. | verification-requirements | Verification Requirements |  | Test |  |  | Integration test to verify interface compliance at system boundaries. Pump cavitation at standby diesel start-up has caused cooling circuit failures in similar nuclear applications; physical flow measurement under load is the only reliable verification method. | verification, engine-cooling, sil-2, session-591, idempotency:ver-ifc022-ec-pump-v2-591
VER-REQ-048 | The Pre-Lube and Post-Lube Pump pre-lubrication functional test SHALL confirm that lubricating oil gallery pressure reaches 1.5 bar within 20 seconds of pre-lube command initiation during factory acceptance testing, with the engine at rest, oil at 20°C ambient temperature, and the start air valve confirm-closed interlock engaged. | verification-requirements | Verification Requirements |  | Test |  |  | Verifies REQ-SEEDGUKNUCLEAR-066: demonstrates that pre-lube timing and pressure specification are met before air start valve is permitted to open, as required for IEEE 387 compliance
VER-REQ-049 | The Engine-Driven Lube Oil Pump pressure performance test SHALL confirm oil gallery pressure within 3.5 bar to 5.5 bar at rated engine speed (750 rpm) across the operating temperature range by measuring main gallery pressure at three oil temperatures: 60°C, 80°C, and 100°C during the 24-hour endurance run. | verification-requirements | Verification Requirements |  | Test |  |  | Verifies REQ-SEEDGUKNUCLEAR-067: temperature-swept pressure measurement during endurance test confirms pump performance at all operating viscosity points; cannot be verified by inspection alone as viscosity-dependent performance requires thermal soak
VER-REQ-050 | The Post-Lube and post-shutdown oil circulation test SHALL confirm that oil gallery pressure remains above 0.8 bar for no less than 10 minutes following a simulated manual shutdown from 100% rated load, with turbocharger inlet temperature measured at 1-minute intervals to confirm thermal purge. | verification-requirements | Verification Requirements |  | Test |  |  | Verifies REQ-SEEDGUKNUCLEAR-070: post-lube duration at minimum pressure is the only way to confirm that turbocharger bearing cartridge heat purge is adequate; analysis alone cannot substitute for empirical thermal measurement
VER-REQ-051 | The Automatic Voltage Regulator steady-state regulation acceptance test SHALL apply step loads at 25%, 50%, 75%, and 100% rated output at power factors of 0.8 lagging and unity, measuring terminal voltage at each steady-state point to confirm it remains within ±1% of 6.6kV (6.534kV to 6.666kV). | verification-requirements | Verification Requirements |  | Test |  |  | Verifies REQ-SEEDGUKNUCLEAR-072: steady-state voltage accuracy at all load points and power factors must be measured empirically; the IEEE Std 387 generator acceptance test protocol requires voltage regulation verification across the full load envelope
VER-REQ-052 | The Automatic Voltage Regulator transient recovery test SHALL apply a block load step equivalent to the largest single load group in the sequencer table while measuring terminal voltage at 100ms intervals, confirming voltage recovery to within ±3% of 6.6kV within 1.5 seconds with no generator protection trip. | verification-requirements | Verification Requirements |  | Test |  |  | Verifies REQ-SEEDGUKNUCLEAR-073: block-load step testing is mandatory per IEEE Std 387 generator acceptance; the 1.5-second window and ±3% recovery threshold must be demonstrated empirically to confirm downstream motor contactor immunity
VER-REQ-053 | The Generator Neutral Earthing Unit design verification SHALL confirm by calculation per IEC 60034-3 that the resistor-loaded transformer limits phase-to-earth fault current to not more than 5 amperes at generator terminal voltage, with the calculation peer-reviewed and included in the safety case documentation. | verification-requirements | Verification Requirements |  | Analysis |  |  | Verifies REQ-SEEDGUKNUCLEAR-074: high-impedance earthing is verified by design analysis rather than fault injection testing, as intentional earth fault injection at generator voltage would risk winding damage; impedance calculation is standard practice per IEC 60034-3 and ONR NS-TAST-GD-013
VER-REQ-054 | The Automatic Voltage Regulator Class 1E qualification inspection SHALL verify by review of the equipment qualification documentation file (EQF) that the AVR has been qualified per IEC 60780 (Class 1E), IEEE Std 344 (seismic at 0.5g/5Hz), and IEEE Std 603 (safety I&C requirements), with certificates reviewed by the Nuclear Licensing Inspector. | verification-requirements | Verification Requirements |  | Inspection |  |  | Verifies REQ-SEEDGUKNUCLEAR-076: Class 1E qualification is verified by inspection of the EQF and qualification test reports; physical re-testing on site is not required provided the original qualification envelope (environment, seismic demand) bounds the as-installed conditions, consistent with ONR ENSREG qualification guidance
VER-REQ-055 | Verify IFC-REQ-023: Pre-heat system functional test during AC blackout simulation. Procedure: disconnect normal AC supply, confirm UPS feed energises heater, measure jacket water temperature over 4 hours from ambient 10°C. Pass criterion: temperature ≥35°C maintained throughout; thermostat cycling within ±2°C hysteresis band. | verification-requirements | Verification Requirements |  | Demonstration |  |  | The pre-heat must remain active during AC blackout precisely when it matters most. A blackout simulation is the only way to verify UPS supply path continuity and thermostat control under actual LOOP event conditions. | verification, engine-cooling, sil-2, session-591, idempotency:ver-ifc023-ec-preheat-v2-591
VER-REQ-056 | Verify IFC-REQ-024: Thermostatic valve response time and flow characteristic test. Apply 10°C step change from 72°C to 85°C at pump inlet; measure valve stroke completion time and flow split at outlet. Pass: full stroke within 5 seconds; bypass flow ≤5% at 82°C; bypass flow ≥95% at 75°C. | verification-requirements | Verification Requirements |  | Test |  |  | The valve stroke response time determines peak coolant temperature overshoot during load steps; measurement at representative temperatures is required to confirm the thermostat characteristic matches design intent. | verification, engine-cooling, sil-2, session-591, idempotency:ver-ifc024-ec-thermostat-v2-591
VER-REQ-057 | Verify IFC-REQ-025: Engine Cooling to I&C signal interface inspection and functional test. Perform cable routing inspection for physical segregation; loop calibration of both Pt100 4-20mA channels against traceable reference; inject simulated overtemperature condition and confirm trip signal received by I&C within 200ms. Pass: segregation verified, channels within ±1°C, trip response ≤200ms. | verification-requirements | Verification Requirements |  | Test |  |  | SIL 2 signal interface requires physical segregation inspection per BS EN 61000 and channel calibration; 200ms trip response is the SIL 2 safety function response time. Only system-level injection test can verify the complete signal chain from sensor to protection relay. | verification, engine-cooling, sil-2, safety-critical, session-591, idempotency:ver-ifc025-ec-ic-signals-591
VER-REQ-058 | Verify SUB-REQ-037 and SUB-REQ-039: Endurance test at 110% rated load, 35°C ambient, for 4 hours minimum. Pass criterion: jacket water outlet temperature 75°C–85°C maintained continuously; no coolant loss; heat exchanger outlet air below design maximum. Instrumentation: 4 Pt100 sensors in jacket water circuit, 2 in radiator airflow. | verification-requirements | Verification Requirements |  | Test |  |  | Combined thermal performance requirements can only be verified together under simultaneous high-load and high-ambient conditions representative of a summer LOOP event. Four hours ensures steady-state thermal equilibrium is reached after the warm-up transient. | verification, engine-cooling, sil-2, session-591, idempotency:ver-sub037-039-ec-thermal-591
VER-REQ-059 | Verify IFC-REQ-026: Fuel Transfer Pump commissioning test. Simulate low Day Tank level (float switch activation), confirm pump starts automatically and delivers fuel at ≥50 L/min to Day Tank. Measure transfer time from low-level alarm to high-level cutoff. Pass: transfer completes within 30 minutes, pump auto-stops on high level, I&C panel shows correct pump status. | verification-requirements | Verification Requirements |  | Test |  |  | The automatic transfer sequence must be verified end-to-end to confirm that float switch, pump control, and I&C monitoring all function correctly together under conditions representative of autonomous engine room operation during a LOOP event. | verification, fuel-oil, sil-2, session-591, idempotency:ver-ifc026-fo-pump-591
VER-REQ-060 | Verify IFC-REQ-027 and SUB-REQ-044: Fuel system endurance and temperature test. Run engine at 100% rated load for 2 hours. Measure fuel inlet pressure and temperature at injection pump inlet at 30-minute intervals. Pass: pressure continuously 0.3–0.7 bar; temperature 10–40°C; no fuel system faults or alarms; engine maintains rated load throughout. | verification-requirements | Verification Requirements |  | Test |  |  | Fuel delivery temperature and pressure must be verified under sustained engine loading to confirm that the EDG building thermal environment and fuel system design maintain the OEM injection pump operating envelope. Short-duration tests do not expose thermal soak effects. | verification, fuel-oil, sil-2, session-591, idempotency:ver-ifc027-fo-supply-591
VER-REQ-061 | Verify IFC-REQ-028 and SUB-REQ-047: Fuel filter differential pressure test. Introduce controlled particulate loading to filter inlet to simulate contaminated fuel. Measure differential pressure and downstream cleanliness (particle count). Pass: alarm activates at 0.5 bar differential; bypass opens at 1.0 bar; downstream cleanliness ≤ISO 4406 16/13/10 below bypass threshold. | verification-requirements | Verification Requirements |  | Test |  |  | Filter performance under contamination conditions is the only means to verify that the bypass valve set-point relationship with the alarm threshold meets the design intent that alarm precedes bypass. Reliance on specification data alone is insufficient for SIL 2 verification. | verification, fuel-oil, sil-2, session-591, idempotency:ver-ifc028-fo-filter-591

## Trace Links
Source Ref | Target Ref | Link Type | Description | Rationale | Created
SYS-REQ-005 | SUB-REQ-060 | derives | Generator Cooling Fan continuous airflow derives from sustained rated-load operation requirement | SYS-REQ-005 24h rated-load endurance requires stator winding temperature to remain within Class H insulation limits; the cooling fan specification is the subsystem mechanism that enables this | 2026-03-27T00:12:44.203Z
SYS-REQ-005 | SUB-REQ-050 | derives | Fuel system standards compliance derives from sustained operation quality and safety requirements | SYS-REQ-005 extended operation requires fuel system components meet ATEX and engineering standards; compliance specification is a direct child of this requirement | 2026-03-27T00:12:37.667Z
SYS-REQ-008 | SUB-REQ-048 | derives | Fuel transfer pump auto-transfer derives from 7-day fuel storage requirement | SYS-REQ-008 requires 7-day fuel autonomy; automatic transfer on low day-tank level is the subsystem mechanism that maintains continuous fuel supply from bulk to day tank | 2026-03-27T00:12:36.902Z
SYS-REQ-005 | SUB-REQ-042 | derives | Thermostatic control valve modulation derives from rated-load coolant temperature requirement | SYS-REQ-005 sustained operation at rated load sets coolant temperature bounds that the thermostatic valve must maintain; valve performance specification derives from this parent | 2026-03-27T00:12:36.193Z
VER-REQ-054 | SUB-REQ-061 | verifies | EQF inspection verifies AVR Class 1E qualification certificates | REQ-083 qualification documentation inspection verifies REQ-076 Class 1E certification | 2026-03-27T00:12:08.829Z
VER-REQ-053 | SUB-REQ-059 | verifies | Design analysis verifies neutral earthing unit limits fault current to 5A | REQ-082 IEC 60034-3 calculation verifies REQ-074 earth fault current limit | 2026-03-27T00:12:08.142Z
VER-REQ-052 | SUB-REQ-058 | verifies | Block-load transient test verifies 1.5s AVR recovery window | REQ-081 block-load test verifies REQ-073 transient voltage recovery specification | 2026-03-27T00:12:07.343Z
VER-REQ-051 | SUB-REQ-057 | verifies | AVR steady-state test verifies voltage regulation ±1% across load envelope | REQ-080 step-load acceptance test verifies REQ-072 AVR steady-state regulation | 2026-03-27T00:12:06.640Z
VER-REQ-050 | SUB-REQ-055 | verifies | Post-lube duration test verifies 10-minute minimum post-shutdown circulation | REQ-079 post-shutdown test verifies REQ-070 post-lube duration and minimum pressure | 2026-03-27T00:12:05.890Z
VER-REQ-049 | SUB-REQ-052 | verifies | Engine-Driven pump pressure test verifies steady-state oil pressure band | REQ-078 temperature-swept test verifies REQ-067 pump pressure specification | 2026-03-27T00:12:05.175Z
VER-REQ-048 | SUB-REQ-051 | verifies | Pre-lube acceptance test verifies pre-lube timing and pressure spec | REQ-077 factory acceptance test verifies REQ-066 pre-lube pump pressure establishment | 2026-03-27T00:12:04.474Z
VER-REQ-061 | SUB-REQ-047 | verifies | Filter test also verifies SUB-REQ-047 contamination class specification | REQ-065 dual-verification covers IFC-REQ-028 and filter contamination class SUB-REQ-047 | 2026-03-27T00:11:50.836Z
VER-REQ-061 | IFC-REQ-028 | verifies | Filter differential pressure test verifies IFC-REQ-028 filter interface | REQ-065 is the verification method for the fuel filter to engine interface | 2026-03-27T00:11:50.160Z
VER-REQ-060 | SUB-REQ-044 | verifies | Fuel endurance test also verifies SUB-REQ-044 fuel delivery pressure | REQ-064 dual-verification covers IFC-REQ-027 and fuel delivery pressure SUB-REQ-044 | 2026-03-27T00:11:49.447Z
VER-REQ-060 | IFC-REQ-027 | verifies | Fuel endurance test verifies IFC-REQ-027 day tank to engine fuel supply | REQ-064 endurance test covers the day tank to engine fuel interface | 2026-03-27T00:11:48.740Z
VER-REQ-059 | IFC-REQ-026 | verifies | Fuel Transfer Pump test verifies IFC-REQ-026 transfer pump to day tank | REQ-063 is the verification method for the fuel transfer pump to day tank interface | 2026-03-27T00:11:47.998Z
VER-REQ-058 | SUB-REQ-039 | verifies | Endurance test also verifies SUB-REQ-039 heat rejection margin | REQ-062 dual-verification covers both SUB-REQ-037 and SUB-REQ-039 | 2026-03-27T00:11:47.272Z
VER-REQ-058 | SUB-REQ-037 | verifies | Endurance test verifies SUB-REQ-037 jacket water temperature band | REQ-062 110% endurance test verifies jacket water temperature band and heat rejection | 2026-03-27T00:11:46.545Z
VER-REQ-057 | IFC-REQ-025 | verifies | Cooling to I&C signal test verifies IFC-REQ-025 interface | REQ-061 is the verification method for the cooling system to I&C signal interface | 2026-03-27T00:11:45.749Z
VER-REQ-056 | IFC-REQ-024 | verifies | Thermostatic valve test verifies IFC-REQ-024 thermostat-to-radiator interface | REQ-060 is the verification method for the thermostatic control valve interface | 2026-03-27T00:11:45.052Z
VER-REQ-055 | IFC-REQ-023 | verifies | Pre-heat system test verifies IFC-REQ-023 pre-heat to jacket water interface | REQ-059 is the verification method for the engine pre-heat circuit interface | 2026-03-27T00:11:44.346Z
VER-REQ-047 | IFC-REQ-022 | verifies | Coolant Pump performance test verifies IFC-REQ-022 pump-to-jacket interface | REQ-058 is the verification method for the coolant circulation pump interface requirement | 2026-03-27T00:11:43.628Z
SUB-REQ-061 | VER-REQ-054 | verifies | EQF inspection verifies AVR Class 1E qualification certificates | REQ-083 qualification documentation inspection verifies REQ-076 Class 1E certification requirement | 2026-03-27T00:09:28.883Z
SUB-REQ-059 | VER-REQ-053 | verifies | Design analysis verifies neutral earthing unit limits fault current to 5A | REQ-082 IEC 60034-3 design calculation verifies REQ-074 earth fault current limit | 2026-03-27T00:09:28.163Z
SUB-REQ-058 | VER-REQ-052 | verifies | Block-load transient test verifies 1.5s recovery window | REQ-081 block-load step test verifies REQ-073 transient voltage recovery specification | 2026-03-27T00:09:27.438Z
SUB-REQ-057 | VER-REQ-051 | verifies | AVR steady-state test verifies voltage regulation ±1% across load envelope | REQ-080 step-load acceptance test verifies REQ-072 AVR steady-state regulation | 2026-03-27T00:09:26.693Z
SUB-REQ-055 | VER-REQ-050 | verifies | Post-lube duration test verifies 10-minute minimum circulation after shutdown | REQ-079 post-shutdown test verifies REQ-070 post-lube duration and minimum pressure | 2026-03-27T00:09:25.985Z
SUB-REQ-052 | VER-REQ-049 | verifies | Engine-Driven pump pressure test verifies steady-state oil pressure band | REQ-078 temperature-swept pressure measurement verifies REQ-067 pump pressure specification | 2026-03-27T00:09:25.133Z
SUB-REQ-051 | VER-REQ-048 | verifies | Pre-lube pressure acceptance test verifies pre-lube timing and pressure spec | REQ-077 is the verification method for REQ-066 pre-lube pump pressure establishment | 2026-03-27T00:09:24.439Z
SYS-REQ-012 | SUB-REQ-061 | derives | Class 1E I&C classification requirement cascades to AVR as active voltage control element | SYS-REQ-012 requires Class 1E qualification for all safety-related I&C; AVR is active during emergency mission, making it safety-related per IEEE 603 scoping criteria | 2026-03-27T00:08:13.819Z
SYS-REQ-006 | SUB-REQ-058 | derives | AVR transient recovery requirement derives from bus voltage stability during load sequencer steps | SYS-REQ-006 combined with load sequencer timing from SUB-REQ-010 determines the 1.5s recovery window to prevent motor contactor dropout | 2026-03-27T00:08:13.107Z
SYS-REQ-006 | SUB-REQ-057 | derives | AVR steady-state regulation derives from bus voltage stability requirement | SYS-REQ-006 voltage band directly constrains AVR regulation accuracy; ±1% steady-state AVR allocation leaves tolerance margin for cable drops and switchgear | 2026-03-27T00:08:12.344Z
SYS-REQ-010 | SUB-REQ-056 | derives | Hardwired engine protection trip matrix includes low lube oil pressure as primary seizure precursor | SYS-REQ-010 requires independent hardwired trip circuits; low lube pressure is a mandatory entry per IEEE 387 and the EDG safety case | 2026-03-27T00:08:11.580Z
SYS-REQ-001 | SUB-REQ-051 | derives | 10-second start requires pre-lube completion before air start valve opens | Start time budget in SYS-REQ-001 must include pre-lube phase; pre-lube timing derives from this constraint | 2026-03-27T00:08:10.882Z
SYS-REQ-005 | SUB-REQ-054 | derives | Filter cleanliness derives from sustained engine reliability requirement | SYS-REQ-005 endurance operation requires maintaining ISO 4406 contamination class; filter specification is the subsystem mechanism that enables this | 2026-03-27T00:08:10.170Z
SYS-REQ-005 | SUB-REQ-053 | derives | Lube oil cooler performance derives from rated-load thermal requirement | SYS-REQ-005 24h rated-load endurance at max ambient sets the thermal load the cooler must handle; oil temperature bounds derived from viscosity analysis at rated BMEP | 2026-03-27T00:08:09.436Z
SYS-REQ-005 | SUB-REQ-051 | derives | Sustained 24h operation requires lube oil system pressure before cranking | Pre-lube requirement derives from 10s start timing and bearing protection SYS requirements | 2026-03-27T00:07:42.957Z
SYS-REQ-005 | SUB-REQ-041 | derives | Coolant pump flow specification derives from sustained rated-load endurance | SYS-REQ-005 requires 24h operation; the specific flow and pressure figures for the Coolant Circulation Pump are derived from the OEM heat balance for the power output mandated by SYS-REQ-005. | 2026-03-26T11:46:20.679Z
SYS-REQ-008 | ARC-REQ-008 | derives | Fuel Oil System architecture decision derives from fuel storage capacity requirement | The two-level storage architecture is the design response to SYS-REQ-008's 7-day fuel inventory mandate combined with the need for reliable engine supply during extended unattended operation. | 2026-03-26T11:46:19.922Z
SYS-REQ-005 | IFC-REQ-028 | derives | Filter to Day Tank interface derives from fuel cleanliness requirement for extended operation | SYS-REQ-005 requires 24h operation; fuel cleanliness is a necessary condition for sustained injection system performance, and the filter interface specification defines how this is maintained during bulk transfer. | 2026-03-26T11:46:19.240Z
SYS-REQ-005 | IFC-REQ-027 | derives | Day Tank to engine fuel supply interface derives from continuous operation at rated load | SYS-REQ-005 mandates 24h operation; the Day Tank to injection system interface specification ensures fuel quality, temperature, and pressure are maintained throughout the endurance period. | 2026-03-26T11:46:18.549Z
SYS-REQ-008 | IFC-REQ-026 | derives | Transfer pump to Day Tank interface derives from 7-day fuel storage and continuous replenishment requirement | SYS-REQ-008 mandates 7-day fuel storage; the transfer pump interface is what moves fuel from bulk storage to the Day Tank to maintain the working inventory throughout an extended LOOP event. | 2026-03-26T11:46:17.836Z
SYS-REQ-005 | IFC-REQ-022 | derives | Coolant pump to jacket water interface derives from sustained rated-load endurance | SYS-REQ-005 requires 24h operation; the coolant pump to jacket water circuit interface specification is what ensures adequate flow and pressure for heat transfer throughout this period. | 2026-03-26T11:46:01.794Z
SYS-REQ-010 | IFC-REQ-025 | derives | Cooling system to I&C signal interface derives from engine protection trip requirement | SYS-REQ-010 mandates hardwired engine protection trips; IFC-REQ-025 defines the specific signal interface through which the cooling system delivers temperature and pressure trip signals to the protection relay. | 2026-03-26T11:46:01.046Z
SYS-REQ-005 | IFC-REQ-024 | derives | Thermostat-radiator interface derives from sustained rated-load operation requirement | SYS-REQ-005 requires 24h operation; the thermostat-radiator bypass control interface is what maintains the jacket water temperature within the operating band during continuous rated-load operation. | 2026-03-26T11:46:00.315Z
SYS-REQ-001 | IFC-REQ-023 | derives | Pre-heat circuit interface derives from 10-second start time requirement | SYS-REQ-001 mandates a 10-second start-to-rated-speed time; the pre-heat interface to the jacket water circuit is the specific mechanism that ensures start reliability across the ambient temperature range. | 2026-03-26T11:45:59.589Z
SYS-REQ-005 | SUB-REQ-046 | derives | Day Tank 4-hour autonomy derives from continuous operation requirement | SYS-REQ-005 requires uninterrupted engine operation; the 4-hour Day Tank buffer is the system's protection against transfer system failures that would otherwise interrupt fuel supply during extended LOOP events. | 2026-03-26T11:43:22.410Z
SYS-REQ-010 | SUB-REQ-049 | derives | Low-fuel safe-state trip derives from engine protection hardwired trip circuits requirement | SYS-REQ-010 mandates independent hardwired trips; the low-fuel injection pump protection trip is the Fuel Oil System's contribution to the engine protection architecture, using the same fail-safe discrete output design. | 2026-03-26T11:43:21.671Z
SYS-REQ-008 | SUB-REQ-045 | derives | Bulk tank 110% inventory margin derives from 7-day fuel storage requirement | SYS-REQ-008 mandates 7-day fuel storage; 110% margin is the specific Fuel Oil System implementation that provides operating margin above the minimum SYS requirement. | 2026-03-26T11:43:20.976Z
SYS-REQ-005 | SUB-REQ-044 | derives | Fuel delivery pressure/flow requirement derives from rated-load 24h endurance | SYS-REQ-005 mandates 24h operation; fuel delivery at correct pressure and flow is the Fuel Oil System's direct contribution to sustaining engine output throughout this period. | 2026-03-26T11:43:20.281Z
IFC-REQ-022 | VER-REQ-001 | verifies | test link | test | 2026-03-26T11:40:59.829Z
VER-REQ-001 | SUB-REQ-001 | verifies | test | test | 2026-03-26T11:40:52.879Z
SYS-REQ-009 | SUB-REQ-043 | derives | Seismic survivability of cooling pressure boundary derives from DBE functional survival | SYS-REQ-009 mandates EDG functionality after a 0.25g DBE; the cooling system must survive as a necessary condition for the engine to run in the post-seismic safe shutdown phase. | 2026-03-26T11:37:04.885Z
SYS-REQ-010 | SUB-REQ-040 | derives | Cooling loss trip derives from engine protection hardwired trip circuits requirement | SYS-REQ-010 mandates independent hardwired trips for engine protection; this is the cooling subsystem's specific trip allocation within that protection architecture, triggered by overtemperature or loss of pressure. | 2026-03-26T11:37:04.146Z
SYS-REQ-005 | SUB-REQ-039 | derives | 110% heat rejection margin derives from rated-load endurance at maximum ambient | SYS-REQ-005 requires sustained operation; 110% thermal margin at 35°C ambient accommodates heat exchanger fouling during multi-day LOOP events without breaching the operating temperature band. | 2026-03-26T11:37:03.455Z
SYS-REQ-001 | SUB-REQ-038 | derives | Pre-heat standby requirement derives from 10-second start time requirement | SYS-REQ-001 requires rated voltage within 10 seconds of start signal; pre-heating jacket water to ≥35°C is the cooling subsystem obligation that enables reliable cold-start performance across the -10°C to 35°C ambient envelope. | 2026-03-26T11:37:02.747Z
SYS-REQ-005 | SUB-REQ-037 | derives | Jacket water temperature band derives from 24h rated-load endurance requirement | SYS-REQ-005 mandates 24h continuous operation at rated load; maintaining the OEM-specified 75–85°C jacket water band is the necessary condition for achieving this without premature engine failure. | 2026-03-26T11:36:45.869Z
SUB-REQ-037 | SUB-REQ-038 | derives | test | test | 2026-03-26T11:36:18.358Z
VER-REQ-044 | SUB-REQ-036 | verifies |  | VER-REQ-044 functional trip test using simulated breach input directly verifies the automatic shutdown requirement in SUB-REQ-036. | 2026-03-26T10:39:54.482Z
VER-REQ-043 | SUB-REQ-032 | verifies |  | VER-REQ-043 airflow measurement test directly verifies the 0.55 kg/s combustion air supply requirement in SUB-REQ-032. | 2026-03-26T10:39:53.832Z
VER-REQ-042 | SUB-REQ-031 | verifies |  | VER-REQ-042 dimensional inspection directly verifies the 600mm inter-train separation requirement in SUB-REQ-031. | 2026-03-26T10:39:53.172Z
VER-REQ-041 | SUB-REQ-033 | verifies |  | VER-REQ-041 criterion (a) requires HVAC fans to reach rated airflow within 30 seconds of EDG start signal, directly verifying the HVAC auto-start timing requirement in SUB-REQ-033. | 2026-03-26T10:39:07.817Z
VER-REQ-041 | SUB-REQ-035 | verifies |  | VER-REQ-041 building integration test includes criterion (c): sump high-level alarm is operational, directly verifying the alarm annunciation requirement in SUB-REQ-035. | 2026-03-26T10:38:17.899Z
VER-REQ-041 | SUB-REQ-034 | verifies |  | VER-REQ-041 building integration test includes criterion (b): exhaust backpressure does not exceed 50 mbar at 100% rated load, directly verifying the backpressure limit in SUB-REQ-034. | 2026-03-26T10:38:17.179Z
SYS-REQ-008 | SUB-REQ-035 | derives |  | Spill containment capacity (110% of 4,000L day tank) derives from SYS-REQ-008 fuel storage requirement; the day tank volume specified in SYS-REQ-008 determines the bund design basis, ensuring that a worst-case day tank failure is fully contained without environmental release or impairment of the alternate EDG train. | 2026-03-26T10:38:16.404Z
SYS-REQ-005 | SUB-REQ-034 | derives |  | Exhaust backpressure limit (50 mbar at turbocharger outlet) derives from SYS-REQ-005 requirement for sustained continuous operation at rated load; excessive backpressure degrades turbocharger efficiency and reduces engine power output, preventing compliance with the 24-hour continuous operation requirement. | 2026-03-26T10:38:05.541Z
SYS-REQ-011 | ARC-REQ-007 | derives |  | Building decomposition ARC decision (SIL allocation per sub-function, HVAC inter-train isolation) derives from SYS-REQ-011 requirement for automatic fire suppression and inter-train fire barriers. | 2026-03-26T10:38:04.823Z
VER-REQ-037 | IFC-REQ-019 | verifies | HVAC-engine air intake commissioning test verifies IFC-REQ-019 | VER-REQ-037 measures combustion air velocity and filter performance at the engine intake plenum — the exact interface quantities specified in IFC-REQ-019. Pass criteria are set at or below the IFC-REQ-019 thresholds of 8 m/s velocity and ePM1 55% filtration efficiency. | 2026-03-26T09:12:56.428Z
VER-REQ-038 | IFC-REQ-020 | verifies | Fire-to-HVAC isolation timing test verifies IFC-REQ-020 | VER-REQ-038 measures end-to-end elapsed time from fire signal generation to damper closure and fan stop — the exact timing criterion of 5 seconds specified in IFC-REQ-020. Three repetitions detect intermittent faults, providing confidence not available from a single-shot test. | 2026-03-26T09:12:56.020Z
VER-REQ-039 | IFC-REQ-021 | verifies | Drain bunding commissioning inspection verifies IFC-REQ-021 | VER-REQ-039 traces the physical drain routing and measures sump capacity — the two criteria in IFC-REQ-021 for continuous bunded containment of the day-tank volume. Inspection is the appropriate method as deliberate release of 4,000L of diesel fuel for a wet test is not acceptable in a nuclear facility. | 2026-03-26T09:12:55.593Z
VER-REQ-040 | SUB-REQ-030 | verifies | Seismic structural analysis verifies building structure anchor deformation requirement | VER-REQ-040 uses Eurocode 8 structural analysis to demonstrate that computed anchor-point deflection stays within the 10mm limit specified in SUB-REQ-030 at the design basis 0.2g PGA loading. Analysis is the only practicable method for a reinforced concrete structure of this scale. | 2026-03-26T09:12:55.157Z
SYS-REQ-009 | SUB-REQ-036 | derives | Seismic operability requirement drives building breach safe-state requirement | SYS-REQ-009 requires EDG functionality after 0.2g PGA. IEC 61508 SIL 2 requires a defined safe state on safety-function failure; SUB-REQ-036 specifies the safe state (isolate and alarm) when the building's physical protection is compromised by seismic or other structural breach. | 2026-03-26T09:12:32.954Z
SYS-REQ-004 | SUB-REQ-032 | derives | Start-on-demand reliability requirement drives HVAC combustion air margin | SYS-REQ-004 mandates 0.975 start-on-demand probability; inadequate combustion air reduces available engine torque and risks failed starts. SUB-REQ-032 implements the combustion air margin needed to preserve start reliability across ambient temperature extremes. | 2026-03-26T09:12:32.276Z
SYS-REQ-001 | SUB-REQ-033 | derives | EDG start timing requirement drives HVAC auto-start timing | SYS-REQ-001 requires EDG at rated voltage within 10 seconds; HVAC must be running before the engine reaches full combustion load at approximately 15-20 seconds. SUB-REQ-033 decomposes this by specifying the HVAC response sequence relative to the engine start signal. | 2026-03-26T09:12:31.534Z
SYS-REQ-007 | SUB-REQ-031 | derives | Train independence requirement drives inter-train fire barrier specification | SYS-REQ-007 mandates two independent redundant trains without common cause failure; fire propagation between trains is the principal building-level common-cause threat. SUB-REQ-031 implements train independence at the physical building level by specifying the minimum fire barrier rating. | 2026-03-26T09:11:11.291Z
SYS-REQ-009 | SUB-REQ-030 | derives | Building seismic integrity requirement derives from system seismic operability requirement | SYS-REQ-009 mandates EDG operability at 0.2g PGA; the Category 1 Building Structure is the primary seismic protection boundary. SUB-REQ-030 directly decomposes this by specifying the maximum permissible anchor-point deformation under design basis seismic load. | 2026-03-26T09:11:10.559Z
VER-REQ-036 | SUB-REQ-029 | verifies | Fire protection commissioning inspection verifies suppression time and fire barrier certification | VER-REQ-036 tests the 30-second actuation criterion from SUB-REQ-029 and verifies the two-hour barrier through certification document review — both criteria in SUB-REQ-029 are addressed. | 2026-03-26T08:40:17.903Z
SYS-REQ-011 | SUB-REQ-029 | derives | EDG building fire suppression and inter-train barrier requirement derives from SYS-REQ-011 | SUB-REQ-029 directly decomposes SYS-REQ-011, specifying the gaseous suppression system type, 30-second extinguishment criterion, and two-hour fire barrier rating for inter-train separation. | 2026-03-26T08:39:57.874Z
VER-REQ-035 | SUB-REQ-022 | verifies | Data diode unidirectionality test verifies no return path to safety I&C | VER-REQ-035 performs a hardware-level electrical injection test from the MCR network side to verify the absence of any return signal path to safety-classified I&C, as required by SUB-REQ-022. | 2026-03-26T08:37:35.357Z
VER-REQ-034 | SUB-REQ-018 | verifies | Pressure alarm and inhibit functional test verifies both threshold actions | VER-REQ-034 tests all three branches of SUB-REQ-018: 27-bar alarm within 5s, 22-bar start inhibit, and inhibit clear on restoration above 25 bar. | 2026-03-26T08:37:34.661Z
VER-REQ-033 | SUB-REQ-017 | verifies | Dewpoint commissioning inspection verifies moisture separator performance | VER-REQ-033 uses chilled-mirror hygrometry to verify the ≤−40°C dewpoint criterion from SUB-REQ-017 after steady-state operation with active separator and auto-drain cycling. | 2026-03-26T08:37:33.935Z
VER-REQ-032 | SUB-REQ-016 | verifies | Air receiver recharge acceptance test verifies compressor recharge capacity | VER-REQ-032 directly tests the 30-bar/30-minute recharge criterion from SUB-REQ-016 by starting from the specified worst-case 20-bar low-pressure condition. | 2026-03-26T08:37:33.220Z
VER-REQ-031 | SUB-REQ-021 | verifies | Class 1E isolation qualification test verifies I/O module isolation and seismic survivability | REQ-SEEDGUKNUCLEAR-050 isolation qualification test directly verifies the 1.5 kV RMS isolation threshold and the post-seismic integrity specified in SUB-REQ-021; both the voltage withstand criterion and the seismic condition are explicitly tested. | 2026-03-26T07:43:09.773Z
VER-REQ-030 | SUB-REQ-028 | verifies | Generator trip circuit test verifies protection trip timing and de-excitation | REQ-SEEDGUKNUCLEAR-049 generator trip circuit timing test directly verifies the de-energise path and terminal voltage collapse timing required by SUB-REQ-028. | 2026-03-26T07:41:29.032Z
VER-REQ-029 | SUB-REQ-027 | verifies | Differential protection test verifies 87G pickup threshold and trip timing | REQ-SEEDGUKNUCLEAR-048 87G differential protection secondary injection test directly verifies the pickup threshold and trip timing specified in SUB-REQ-027. | 2026-03-26T07:41:28.309Z
VER-REQ-028 | SUB-REQ-025 | verifies | GCB acceptance test verifies 100ms close-time requirement | REQ-SEEDGUKNUCLEAR-047 GCB close-time acceptance test directly verifies the 100ms close-time constraint in SUB-REQ-025; pass/fail measured against the same threshold. | 2026-03-26T07:41:27.607Z
VER-REQ-005 | SUB-REQ-015 | verifies | Starting Air interface test confirms air start valve opening performance | VER-REQ-005 Starting Air System interface test confirms 25–30 bar pressure at the distributor inlet and measures cranking torque; this test sequence requires the air start valve (SUB-REQ-015) to fully open to the distributor, making valve response time an implicit pass/fail criterion. | 2026-03-26T07:39:49.553Z
VER-REQ-011 | SUB-REQ-013 | verifies | Fuel Injection System test under Class 1E supply verifies power supply requirement | VER-REQ-011 Fuel Injection System acceptance test operates the injection system from its qualified power supply under full load; this test configuration inherently verifies SUB-REQ-013's Class 1E 24VDC supply requirement because failure of that supply during the test would manifest as injection loss. | 2026-03-26T07:39:48.871Z
VER-REQ-002 | SUB-REQ-012 | verifies | Engine Protection Relay Package test verifies fail-safe architecture | VER-REQ-002 functional test of each protection relay trip confirms both the individual setpoint accuracy (SUB-REQ-004/005/006) and the fail-safe de-energise-to-trip relay architecture required by SUB-REQ-012; the same test article exercises the full relay package. | 2026-03-26T07:39:37.970Z
VER-REQ-011 | SUB-REQ-007 | verifies | Combustion analyser metering test verifies ±3% fuel variation requirement | VER-REQ-011 is the test procedure that directly verifies the fuel injection metering criterion in SUB-REQ-007. Test method is measurement under the same conditions the requirement specifies (steady-state rated load). | 2026-03-26T07:34:48.526Z
VER-REQ-012 | SUB-REQ-011 | verifies | Tank volume inspection verifies 7,000-litre minimum fuel inventory | VER-REQ-012 provides physical measurement verification of the fuel inventory requirement in SUB-REQ-011. The inspection method is appropriate as tank gauging is the standard quantitative method for fuel inventory confirmation. | 2026-03-26T07:34:48.121Z
VER-REQ-013 | IFC-REQ-003 | verifies | UHS cooling flow test verifies EDG-to-UHS thermal interface performance | VER-REQ-013 tests at the rated-load safety-significant condition matching IFC-REQ-003 acceptance criteria of 150 m³/h at ≤30°C. | 2026-03-26T07:34:47.716Z
VER-REQ-014 | IFC-REQ-005 | verifies | MCR interface functional test verifies all alarm, display, and command channels | VER-REQ-014 functionally tests every channel in IFC-REQ-005 — the only way to confirm Class 1E cabling integrity end-to-end before plant operation. | 2026-03-26T07:34:47.307Z
VER-REQ-015 | IFC-REQ-006 | verifies | Fuel supply demonstration verifies overfill protection and day tank reserve | VER-REQ-015 demonstrates both the overfill protection and 2-hour day tank reserve jointly specified in IFC-REQ-006. | 2026-03-26T07:34:46.891Z
VER-REQ-016 | IFC-REQ-007 | verifies | DC battery interface test verifies 125VDC supply and charger feedback under LOOP | VER-REQ-016 tests the safety-critical charger feedback loop that cannot be validated by inspection, as required by IFC-REQ-007 extended LOOP scenario. | 2026-03-26T07:34:46.483Z
VER-REQ-017 | SUB-REQ-014 | verifies | Receiver pressure acceptance test verifies SAS capacity requirement | Direct pressure and capacity test confirms receiver sizing — analysis cannot account for as-built valve and piping losses. | 2026-03-26T07:34:46.071Z
VER-REQ-018 | SUB-REQ-019 | verifies | LOOP detection timing test verifies I&C start command latency | Timing measurements at system boundary confirm the timing budget allocation assumptions. | 2026-03-26T07:34:45.645Z
VER-REQ-019 | SUB-REQ-020 | verifies | Protection trip timing test verifies I&C response latency | Hardware-in-the-loop testing at 0.1 ms resolution confirms SIL 3 trip latency. | 2026-03-26T07:34:45.247Z
VER-REQ-020 | SUB-REQ-023 | verifies | I&C safe-state test verifies de-energise-to-trip transition | IEC 61508 SIL 3 requires verified safe-state transition. Test confirms all three safe-state outputs are achieved within specified timing. | 2026-03-26T07:34:44.794Z
VER-REQ-021 | IFC-REQ-014 | verifies | Integration test verifies I&C to SAS start command interface | IFC-REQ-014 requires 200 ms timing and Class 1E power at the interface; VER-REQ-021 tests both under simulated loss-of-normal-power conditions as specified. | 2026-03-26T07:34:44.394Z
VER-REQ-022 | IFC-REQ-015 | verifies | SAS pressure monitoring interface test verifies IFC-REQ-015 | Tests both analogue and discrete paths independently to catch masked failures where only one path is functional. | 2026-03-26T07:34:43.960Z
VER-REQ-027 | IFC-REQ-017 | verifies | Sync check relay close permission acceptance test verifies IFC-REQ-017 | VER-REQ-027 covers boundary conditions, anti-pumping, and permission withdrawal - the three behavioural aspects of IFC-REQ-017. Together they provide necessary and sufficient coverage. | 2026-03-26T07:10:39.438Z
SYS-REQ-010 | SUB-REQ-028 | derives | Switchgear safe state derives from hardwired engine and generator protection requirement | SUB-REQ-028 derives from SYS-REQ-010's overcurrent trip requirement: when the Generator Electrical Protection Relay Package issues a trip signal, the switchgear must open the GCB within 200ms and inhibit re-close, completing the hardwired trip chain from detection to load isolation. | 2026-03-26T07:10:37.956Z
VER-REQ-026 | IFC-REQ-018 | verifies | GEPRP to GCB trip circuit test verifies IFC-REQ-018 resistance, supervision, and trip timing | VER-REQ-026 tests the three measurable aspects of IFC-REQ-018 at both nominal and minimum battery voltage, which is required by IEC 61508 SIL 3 hardware validation. The resistance, supervision, and timing tests address distinct failure modes. | 2026-03-26T07:08:43.486Z
VER-REQ-025 | IFC-REQ-016 | verifies | BUVR to GCB interface integration test verifies IFC-REQ-016 resistance, failsafe, and segregation | VER-REQ-025 covers all three acceptance criteria of IFC-REQ-016 through three complementary test methods: resistance measurement, functional failsafe test, and visual inspection of segregation. Together they provide complete coverage. | 2026-03-26T07:08:42.828Z
VER-REQ-024 | SUB-REQ-026 | verifies | Sync check relay acceptance test verifies SUB-REQ-026 synchronising windows and dead-bus override | VER-REQ-024 tests all boundary conditions and the dead-bus override scenario, covering both the synchronising window limits and the LOOP detection override that are the two distinct aspects of SUB-REQ-026. | 2026-03-26T07:08:42.136Z
VER-REQ-023 | SUB-REQ-024 | verifies | BUVR factory acceptance test verifies SUB-REQ-024 detection threshold and voting logic | VER-REQ-023 tests three scenarios that together cover all acceptance criteria of SUB-REQ-024: threshold, transient rejection, and voting. The test is necessary and sufficient to demonstrate compliance. | 2026-03-26T07:08:41.436Z
SYS-REQ-010 | SUB-REQ-027 | derives | Generator electrical protection implements hardwired protection requirement | SUB-REQ-027 implements the overcurrent trip function from SYS-REQ-010, specifying differential (87G), overcurrent (51), loss-of-excitation (40), and reverse power (32) relay functions with hardwired trip signals to the GCB within 100ms, extending SYS-REQ-010 to the generator electrical domain. | 2026-03-26T07:07:10.344Z
SYS-REQ-003 | SUB-REQ-026 | derives | Sync check relay conditions govern GCB closure enabling load connection | SYS-REQ-003 requires connection of safety loads to the emergency bus; SUB-REQ-026 specifies the synchronising conditions for GCB closure that are the prerequisite for load connection. Dead-bus override ensures the LOOP scenario does not block the safety function. | 2026-03-26T07:07:09.641Z
SYS-REQ-001 | SUB-REQ-025 | derives | GCB close time allocated from 10-second bus restoration budget | SYS-REQ-001 requires bus restoration within 10 seconds; SUB-REQ-025 allocates 100ms to GCB mechanical operation within that budget. The GCB is on the critical path and its timing is a direct decomposition of the system-level deadline. | 2026-03-26T07:07:08.989Z
SYS-REQ-002 | SUB-REQ-024 | derives | BUVR detection derives from automatic start on bus undervoltage | SUB-REQ-024 specifies the Bus Undervoltage Sensing Relay threshold and two-out-of-three voting that directly implements SYS-REQ-002's automatic start function. The 4.6kV and 200ms parameters are the quantified expression of the system-level start-on-LOOP requirement. | 2026-03-26T07:07:08.262Z
SYS-REQ-012 | SUB-REQ-022 | derives | Data diode isolation derives from safety system network isolation requirement | SYS-REQ-012 requires isolation from non-safety networks; SUB-REQ-022 implements unidirectional data diode as the only hardware-enforced isolation. | 2026-03-26T06:40:00.691Z
SYS-REQ-012 | SUB-REQ-021 | derives | Class 1E I/O isolation derives from safety system isolation requirement | SYS-REQ-012 requires isolation from non-safety networks; SUB-REQ-021 implements this at the I/O module with 1.5 kV RMS dielectric test and seismic qualification. | 2026-03-26T06:40:00.036Z
SYS-REQ-009 | SUB-REQ-017 | derives | Moisture separator dewpoint derived from environmental survivability requirement | SYS-REQ-009 requires EDG function at minimum 5 C site ambient; dewpoint control prevents freeze-up in the air start distributor at that temperature. | 2026-03-26T06:39:48.477Z
SYS-REQ-013 | SUB-REQ-016 | derives | Compressor recharge time derived from surveillance testing operability return | 30-minute recharge enables return to operability within one hour of monthly surveillance test completion. | 2026-03-26T06:39:47.781Z
SYS-REQ-001 | SUB-REQ-015 | derives | Valve actuation timing derived from 10-second start budget | 0.5 s valve actuation is allocated from the 10-second start-to-rated-voltage budget as the dominant latency in the start chain. | 2026-03-26T06:39:47.114Z
SYS-REQ-004 | SUB-REQ-014 | derives | SAS receiver pressure derives from start reliability requirement | Three-attempt capacity and 25 bar minimum pressure are necessary to achieve 0.975 start-on-demand reliability derived in SYS-REQ-004. | 2026-03-26T06:39:46.403Z
SYS-REQ-010 | SUB-REQ-012 | derives | Fail-safe de-energise-to-trip relay architecture derives from hardwired engine protection requirement | SUB-REQ-012 derives from SYS-REQ-010's 'independent, hardwired trip circuits' requirement: it specifies the de-energise-to-trip architecture ensuring that loss of 125VDC control power causes engine trip rather than spurious protection bypass, satisfying the independence mandate. | 2026-03-26T06:08:28.585Z
SYS-REQ-005 | ARC-REQ-006 | derives | Separate cooling architecture realises sustained operation system requirement | ARC-REQ-006 (separate cooling subsystem with independent fault tree for SIL 2 hazard H-006) is the architecture decision realising SYS-REQ-005 sustained continuous operation. Separating cooling from the engine assembly enables targeted redundancy measures (standby fan, independent thermostat) that are required to achieve the availability target under the SIL 2 cooling failure hazard classification. | 2026-03-26T04:43:10.626Z
SYS-REQ-003 | ARC-REQ-005 | derives | Switchgear integration architecture realises load sequencing system requirement | ARC-REQ-005 (integrating LOOP detection, generator breaker control, and load sequencing in one subsystem) is the architecture decision realising SYS-REQ-003 priority-based load sequencing. Grouping these functions eliminates the inter-subsystem latency and race conditions that could cause load sequencing errors, and enables single-point testing per IEEE 387. | 2026-03-26T04:43:09.974Z
SYS-REQ-002 | ARC-REQ-004 | derives | Pneumatic starting architecture realises automatic start system requirement | ARC-REQ-004 (compressed-air starting with 5 consecutive attempts) is the architecture decision realising SYS-REQ-002 automatic start on LOOP detection. Compressed air provides the consistent cranking torque at all ambient temperatures required for automatic start reliability; sizing for 5 consecutive attempts ensures the reliability target can be met even if the first attempt fails. | 2026-03-26T04:43:09.288Z
SYS-REQ-001 | ARC-REQ-001 | derives | Medium-speed diesel architecture realises 10-second start system requirement | ARC-REQ-001 (medium-speed 4-stroke turbocharged diesel at 750/1000 rpm achieving 0.975 start-on-demand probability) is the architecture decision that realises SYS-REQ-001 10-second start-to-rated-output requirement. Medium-speed diesel engines achieve the combination of start reliability and rated-output delivery time required by the system requirement. | 2026-03-26T04:42:53.296Z
SYS-REQ-012 | ARC-REQ-002 | derives | Hardwired protection architecture realises cybersecurity isolation system requirement | ARC-REQ-002 (hardwired relay protection circuits physically separate from digital monitoring and control) is the architecture decision that realises SYS-REQ-012 cybersecurity isolation. Hardware separation is the implementation mechanism eliminating software attack surface from the safety trip path. | 2026-03-26T04:42:52.656Z
SYS-REQ-007 | ARC-REQ-003 | derives | Train independence architecture realises two-train redundancy system requirement | ARC-REQ-003 (physically independent trains A and B in separate fire-rated buildings) is the architecture decision that realises SYS-REQ-007 two-train redundancy. Physical separation in fire-rated buildings is the implementation mechanism that achieves the independence mandate at all levels of the system. | 2026-03-26T04:42:51.976Z
VER-REQ-006 | IFC-REQ-004 | verifies | End-to-end start chain test verifies the PPS-to-EDG LOOP signal interface | VER-REQ-006 end-to-end start chain test verifies IFC-REQ-004 (Plant Protection System interface) because the simulated LOOP signal injected in the test replicates the PPS undervoltage output that initiates the start sequence. Confirming LOOP detection within 100 ms demonstrates the electrical interface between the PPS output and the LOOP detection relay functions within specification. | 2026-03-26T04:41:28.316Z
VER-REQ-002 | IFC-REQ-012 | verifies | Protection relay functional test verifies the engine-instrumentation interface | VER-REQ-002 Engine Protection Relay Package functional test verifies IFC-REQ-012 (engine-I&C interface) because it exercises the signal path from each sensor to the relay and from the relay trip output to the fuel rack. Confirming relay actuation within 2 seconds with the digital system de-energised confirms the hardwired interface path between the engine instrumentation and the protection system functions correctly. | 2026-03-26T04:41:27.616Z
VER-REQ-007 | IFC-REQ-013 | verifies | 24-hour endurance test verifies the crankshaft-to-generator mechanical coupling | VER-REQ-007 24-hour endurance test verifies IFC-REQ-013 (crankshaft-to-generator flexible coupling interface) because continuous transmission of rated torque for 24 hours is the primary stress case for the flexible coupling. Vibration signatures and alignment drift are measurable during the endurance run, and any mechanical weakness in the coupling will manifest as abnormal vibration or coupling fatigue before the test duration completes. | 2026-03-26T04:41:26.949Z
VER-REQ-007 | IFC-REQ-010 | verifies | 24-hour endurance test verifies the engine-lube oil system interface | VER-REQ-007 24-hour endurance test verifies IFC-REQ-010 (engine-lube oil system interface) because continuous loaded operation at rated output subjects the lube oil circuit to its worst-case flow and pressure demands. Oil degradation, pressure drop across the filter, and bearing feed pressure are all observable during the 24-hour test and will confirm compliance with the OEM lube oil interface specification. | 2026-03-26T04:41:12.009Z
VER-REQ-007 | IFC-REQ-009 | verifies | 24-hour endurance test verifies the engine-cooling system thermal interface | VER-REQ-007 24-hour endurance test verifies IFC-REQ-009 (engine-cooling system interface) because sustained operation at rated output exercises the full cooling loop: coolant flow rate, heat rejection to the radiator, thermostat opening and closing cycles, and pump head pressure are all stressed continuously. Any interface deficiency (coolant starvation, pump cavitation, thermostat hunt) will manifest before the 24-hour mark. | 2026-03-26T04:41:11.341Z
SYS-REQ-015 | IFC-REQ-005 | derives | Diverse AC connection capability requires MCR interface support for operator switchover | SYS-REQ-015 diverse alternate AC source requires operator visibility and switchover capability at the Main Control Room. IFC-REQ-005 (MCR interface) must support the connection of a mobile diesel generator within 4 hours: the operator needs status information on the alternate AC connection point and breaker control from the MCR to execute this function within the time constraint. | 2026-03-26T04:40:58.809Z
SYS-REQ-012 | SUB-REQ-004 | derives | Cyber isolation system requirement derives to hardwired overspeed relay subsystem req | SYS-REQ-012 cybersecurity isolation (hardwired protection, no software defeat path) derives to SUB-REQ-004 overspeed relay because the relay implements one of the three protection functions that must operate independently of any digital system. SUB-REQ-004 specifies relay actuation independent of the monitoring and control digital system, realising the cyber isolation requirement at the subsystem level. | 2026-03-26T04:40:58.138Z
SYS-REQ-014 | SUB-REQ-003 | derives | Single train 100% load capability requires each engine to sustain full rated output | SYS-REQ-014 requires each train to supply 100 percent of safety-critical electrical load when the other is inoperable. This N+1 redundancy requirement directly drives SUB-REQ-003: each engine must sustain rated continuous mechanical power output at 100 percent, because neither train can rely on the other for load sharing during the worst-case single-failure scenario. | 2026-03-26T04:40:39.092Z
SYS-REQ-004 | SUB-REQ-001 | derives | System reliability target allocates to engine start criterion | SYS-REQ-004 start-on-demand reliability of 0.975 is primarily driven by the engine start subsystem. SUB-REQ-001 (self-sustaining rotation within 3 seconds) is the critical path for start reliability: any failure to self-sustain is a demand failure. The 0.975 target allocates the dominant failure probability budget to this subfunction. | 2026-03-26T04:40:21.140Z
STK-REQ-015 | SYS-REQ-010 | derives | Failure prevention stakeholder need derives hardwired protection trip specification | STK-REQ-015 requires no EDG failure mode to contribute to an uncontrolled shutdown; SYS-REQ-010 derives from this by specifying hardwired overspeed (>115%) and over-temperature trip circuits that protect against runaway failure modes. | 2026-03-26T04:40:03.401Z
STK-REQ-005 | SYS-REQ-008 | derives | SBO procedure support need drives 7-day autonomous fuel inventory specification | STK-REQ-005 requires supporting SBO emergency procedures; SYS-REQ-008 derives the 7-day fuel autonomy specification that ensures EDG sustains operation through the full SBO recovery scenario without external fuel resupply. | 2026-03-26T04:40:02.725Z
STK-REQ-012 | SYS-REQ-006 | derives | Voltage regulation requirement derives from stakeholder reliability requirement | SYS-REQ-006 voltage and frequency regulation derives from STK-REQ-012 start-on-demand reliability: a generator that starts but fails to hold voltage within 10 percent of nominal or frequency within 2 percent cannot deliver safety loads. Voltage and frequency limits are the engineering operationalisation of reliable power supply. | 2026-03-26T04:39:52.798Z
VER-REQ-010 | SUB-REQ-010 | verifies | Load sequencer test verifies priority-based load connection sequence | VER-REQ-010 tests the first-priority load group connection timing defined by SUB-REQ-010. | 2026-03-26T02:09:29.198Z
VER-REQ-009 | SUB-REQ-008 | verifies | Seismic qualification analysis verifies engine assembly seismic resistance | VER-REQ-009 seismic analysis verifies the seismic category and anchorage specified in SUB-REQ-008. | 2026-03-26T02:09:08.909Z
VER-REQ-008 | IFC-REQ-002 | verifies | EDG automatic start test verifies LOOP detection and bus energisation timing | VER-REQ-008 verifies automatic start including the EDG-to-Emergency-AC-Bus interface voltage and frequency criteria in IFC-REQ-002. | 2026-03-26T02:09:08.234Z
VER-REQ-008 | IFC-REQ-001 | verifies | EDG automatic start test verifies LOOP detection interface with National Grid monitor | VER-REQ-008 verifies the LOOP detection signal interface defined in IFC-REQ-001 as part of the end-to-end start chain. | 2026-03-26T02:09:07.564Z
VER-REQ-007 | SUB-REQ-003 | verifies | 24-hour endurance test verifies engine steady-state speed regulation | VER-REQ-007 endurance test conditions include rated load at which SUB-REQ-003 sustained power output is verified. | 2026-03-26T02:08:33.582Z
VER-REQ-007 | SUB-REQ-002 | verifies | 24-hour endurance test verifies engine speed regulation within ±1.5 rpm | VER-REQ-007 sustained load test is the method that verifies SUB-REQ-002 speed regulation — speed is monitored continuously throughout the 24-hour run. | 2026-03-26T02:08:32.803Z
VER-REQ-006 | SUB-REQ-001 | verifies | End-to-end start chain test verifies cold start self-sustaining rotation requirement | VER-REQ-006 start chain test encompasses the engine start function, verifying the self-sustaining rotation criterion in SUB-REQ-001 within the 10-second system budget. | 2026-03-26T02:07:52.783Z
SYS-REQ-005 | SUB-REQ-007 | derives | 24-hour endurance requirement derives to fuel injection system metering criterion | SYS-REQ-005 sustained 24-hour operation at rated load requires fuel injection to maintain ±3% cylinder-to-cylinder balance throughout — this is the direct engineering basis for SUB-REQ-007. | 2026-03-26T02:07:52.101Z
SYS-REQ-001 | IFC-REQ-013 | derives | 10-second start performance requirement derives to generator-to-bus coupling interface | SYS-REQ-001 requires the generator to be synchronised and connected within 10 seconds; IFC-REQ-013 specifies the crankshaft-to-generator mechanical coupling that must sustain this transient torque. | 2026-03-26T02:07:24.589Z
SYS-REQ-010 | IFC-REQ-012 | derives | Hardwired engine protection requirement derives to EDG instrumentation and control interface | IFC-REQ-012 derives from SYS-REQ-010 to define the physical signal interface through which each hardwired trip function status (overspeed, high coolant temp, low oil pressure, overcurrent) is transmitted as a 24VDC discrete input from the Engine Protection Relay Package to the I&C system. | 2026-03-26T02:07:23.934Z
SYS-REQ-005 | IFC-REQ-010 | derives | 24-hour operation requirement derives to lube oil system interface for engine protection | SYS-REQ-005 sustained operation requires continuous lubrication; IFC-REQ-010 specifies the lubrication oil interface pressure and cleanliness criteria that protect bearing surfaces during the mission. | 2026-03-26T02:07:10.853Z
SYS-REQ-005 | IFC-REQ-009 | derives | 24-hour operation requirement derives to engine cooling interface thermal performance | SYS-REQ-005 sustained operation at rated load requires cooling system performance; IFC-REQ-009 specifies the jacket water thermal interface that limits engine block temperature. | 2026-03-26T02:07:10.183Z
SYS-REQ-008 | SUB-REQ-011 | derives | Fuel storage capacity requirement derives to fuel oil system inventory subsystem | SYS-REQ-008 specifies 7-day fuel capacity at system level; SUB-REQ-011 is the subsystem implementation of that capacity in terms of actual tank volumes, fuel specification, and transfer management. | 2026-03-26T02:07:09.479Z
SYS-REQ-003 | SUB-REQ-010 | derives | Load sequencing requirement derives to switchgear and load sequencer subsystem | SYS-REQ-003 requires priority-based load connection; SUB-REQ-010 specifies the switchgear subsystem that implements the sequencer with connection timing for each priority group. | 2026-03-26T02:06:56.299Z
STK-REQ-013 | SYS-REQ-007 | derives | Qualification evidence requirement derives to dual-train redundancy system architecture | STK-REQ-013 requires maintenance of original qualification throughout plant life; SYS-REQ-007 derives this as a two-train independent architecture requirement to simplify re-qualification when modifications affect one train only. | 2026-03-26T02:06:30.467Z
STK-REQ-018 | SYS-REQ-015 | derives | EMC requirement derives to diverse AC power source for SBO | STK-REQ-018 requires no EMI-induced spurious trips; SYS-REQ-015 provides a diverse AC source that remains available even if EMI causes loss of the primary EDG control system. | 2026-03-26T02:06:21.964Z
STK-REQ-017 | SYS-REQ-005 | derives | Ambient temperature range requirement derives to 24-hour mission endurance requirement | STK-REQ-017 requires operation across full UK ambient range (-15°C to +40°C); SYS-REQ-005 sustained 24-hour operation must be demonstrated across this envelope, driving cooling and lubrication system specifications. | 2026-03-26T02:06:21.307Z
STK-REQ-014 | SYS-REQ-005 | derives | OEM maintenance interval requirement derives to 24-hour mission endurance requirement | STK-REQ-014 requires OEM maintenance intervals; SYS-REQ-005 sustained endurance at rated load is the operational profile that determines maintenance interval compliance and engine wear rate. | 2026-03-26T02:06:20.674Z
STK-REQ-011 | SYS-REQ-003 | derives | Deterministic safety case need drives load sequencer specification | STK-REQ-011 requires a deterministic safety case demonstrating that the EDG performs its safety function; SYS-REQ-003 derives the load sequencer requirement which ensures deterministic load pick-up order, preventing bus overload failures that would void the safety case. | 2026-03-26T02:06:19.618Z
STK-REQ-009 | SYS-REQ-012 | derives | Diagnostic access requirement derives to cyber-secure control system requirement | STK-REQ-009 requires diagnostic access to setpoints; SYS-REQ-012 addresses this through qualified access controls compliant with IEC 62645 that allow calibration without compromising cybersecurity. | 2026-03-26T02:06:02.736Z
STK-REQ-008 | SYS-REQ-013 | derives | Calibration and test requirement derives to monthly surveillance test requirement | STK-REQ-008 requires calibration and functional testing support; SYS-REQ-013 specifies the monthly fast-start surveillance test that is the primary test regime satisfying this stakeholder need. | 2026-03-26T02:06:02.007Z
STK-REQ-007 | SYS-REQ-011 | derives | Train isolation maintenance need drives inter-train fire barrier specification | STK-REQ-007 requires maintenance isolation via LOTO provisions; SYS-REQ-011 derives the inter-train fire barrier and suppression requirement that ensures safe maintenance on one train without compromising the other train's operability. | 2026-03-26T02:06:01.313Z
STK-REQ-006 | SYS-REQ-012 | derives | Fault diagnosis requirement derives to cyber-secure control system requirement | STK-REQ-006 requires local fault diagnosis capability; SYS-REQ-012 qualified access to control system provides the diagnostic access needed without creating unmonitored cyber pathways. | 2026-03-26T02:06:00.594Z
STK-REQ-005 | SYS-REQ-013 | derives | SBO support requirement derives to monthly surveillance test | STK-REQ-005 requires SBO blackout start capability; SYS-REQ-013 monthly testing validates the blackout start sequence that ensures the system is available for the SBO scenario. | 2026-03-26T02:05:47.541Z
STK-REQ-002 | SYS-REQ-013 | derives | Operator control requirement derives to monthly surveillance and test requirement | STK-REQ-002 requires operator manual start/stop; SYS-REQ-013 tests the manual start command interface as part of surveillance testing, confirming the command path is functional. | 2026-03-26T02:05:46.840Z
SYS-REQ-007 | IFC-REQ-007 | derives | Two-train redundancy requirement derives to DC battery system interface | SYS-REQ-007 requires independent train redundancy; IFC-REQ-007 specifies the DC battery interface that provides electrically independent control power for each train, eliminating common-cause DC failure. | 2026-03-26T02:05:34.649Z
SYS-REQ-008 | IFC-REQ-006 | derives | Fuel storage requirement derives to fuel supply infrastructure fill interface | SYS-REQ-008 requires 7-day fuel storage; IFC-REQ-006 specifies the external supply interface that enables periodic fuel top-up to maintain the inventory requirement, including overfill protection. | 2026-03-26T02:05:34.005Z
SYS-REQ-013 | IFC-REQ-005 | derives | Surveillance test requirement derives to MCR monitoring and command interface | SYS-REQ-013 requires monthly start surveillance tests; IFC-REQ-005 MCR interface provides the operator command capability to initiate and monitor the monthly test from the control room. | 2026-03-26T02:05:33.338Z
SYS-REQ-002 | IFC-REQ-004 | derives | Automatic start requirement derives to plant protection system signal interface | SYS-REQ-002 requires automatic LOOP-triggered start; IFC-REQ-004 specifies the electrical interface with the PPS that delivers the start demand signal to the EDG control system. | 2026-03-26T02:05:32.659Z
SYS-REQ-005 | IFC-REQ-003 | derives | 24-hour endurance requirement derives to ultimate heat sink cooling water interface | SYS-REQ-005 sustained 24-hour full-load operation requires continuous heat rejection; IFC-REQ-003 specifies the external cooling water interface with the UHS that provides that heat rejection. | 2026-03-26T02:05:32.017Z
SYS-REQ-001 | IFC-REQ-002 | derives | 10-second start requirement derives to emergency AC bus voltage and frequency interface | SYS-REQ-001 specifies 6.6kV ±10% at rated frequency within 10 seconds; IFC-REQ-002 defines the exact electrical interface parameters at the emergency AC bus connection point that satisfy this requirement. | 2026-03-26T02:05:16.076Z
SYS-REQ-002 | IFC-REQ-001 | derives | Automatic LOOP detection requirement derives to national grid loss-of-supply interface | SYS-REQ-002 requires automatic start on LOOP detection; IFC-REQ-001 specifies the voltage/frequency monitoring interface with the national grid connection that detects the LOOP condition and initiates the start sequence. | 2026-03-26T02:05:15.026Z
VER-REQ-001 | SUB-REQ-001 | verifies | Cold start acceptance test verifies engine start self-sustain budget | VER-REQ-001 provides direct measurement of the 3-second self-sustain criterion at worst-case temperature, which is the acceptance criterion for SUB-REQ-001. | 2026-03-26T02:01:58.501Z
VER-REQ-002 | SUB-REQ-004 | verifies | Protection trip test verifies hardwired trip function | VER-REQ-002 tests each of the three protection trip channels independently, covering the setpoint and response time criteria in SUB-REQ-004, 005, and 006. | 2026-03-26T02:01:58.052Z
VER-REQ-002 | SUB-REQ-005 | verifies | Protection trip test verifies hardwired trip function | VER-REQ-002 tests each of the three protection trip channels independently, covering the setpoint and response time criteria in SUB-REQ-004, 005, and 006. | 2026-03-26T02:01:57.612Z
VER-REQ-002 | SUB-REQ-006 | verifies | Protection trip test verifies hardwired trip function | VER-REQ-002 tests each of the three protection trip channels independently, covering the setpoint and response time criteria in SUB-REQ-004, 005, and 006. | 2026-03-26T02:01:57.148Z
VER-REQ-003 | SUB-REQ-009 | verifies | Safe state test verifies engine transition to standstill within 5 seconds | VER-REQ-003 measures engine standstill time under load for all three trip channels, directly testing the safe-state transition time criterion in SUB-REQ-009. | 2026-03-26T02:01:56.696Z
VER-REQ-004 | IFC-REQ-008 | verifies | Fuel supply test verifies injection pump inlet pressure and cleanliness | VER-REQ-004 directly measures the pressure and cleanliness parameters specified in IFC-REQ-008 at the injection pump inlet under rated load. | 2026-03-26T02:01:56.212Z
VER-REQ-005 | IFC-REQ-011 | verifies | Air start test verifies distributor inlet pressure and cranking speed | VER-REQ-005 measures both the air pressure and cranking speed at minimum ambient temperature, directly testing the IFC-REQ-011 acceptance criteria. | 2026-03-26T02:01:55.770Z
STK-REQ-010 | SYS-REQ-012 | derives | ONR SAP compliance need drives network isolation specification | STK-REQ-010 requires ONR SAP compliance including EDG-2 (separation from non-nuclear systems); SYS-REQ-012 derives the specific cybersecurity isolation boundary ensuring no non-safety network can affect EDG control functions. | 2026-03-26T01:45:42.019Z
STK-REQ-016 | SYS-REQ-009 | derives | Site DBE operability need directly derives seismic qualification requirement | STK-REQ-016 establishes the stakeholder requirement for 0.2g DBE operability at the UK licensed site; SYS-REQ-009 converts this into the binding seismic qualification requirement specifying IEEE 344 analysis and OBE fragility criteria. | 2026-03-26T01:45:40.500Z
STK-REQ-012 | SYS-REQ-004 | derives | Stakeholder reliability target directly derives system reliability criterion | STK-REQ-012 sets the stakeholder reliability target of 0.975 start-on-demand, directly flowing down to SYS-REQ-004 which formalises this as a binding system-level probabilistic criterion with demonstration via fault tree analysis. | 2026-03-26T01:45:39.347Z
SYS-REQ-009 | SUB-REQ-008 | derives | Engine seismic qualification from system seismic requirement | SYS-REQ-009 requires Seismic Category I for the system; SUB-REQ-008 decomposes this to the engine assembly with its specific seismic challenges. | 2026-03-26T01:43:09.345Z
SYS-REQ-010 | SUB-REQ-009 | derives | Hardwired trip function decomposed from system trip requirement | SUB-REQ-009 derives from SYS-REQ-010 to specify the Diesel Engine Assembly's mandatory safe-state response to any trip signal — all fuel injection ceased, deceleration to standstill within 5 seconds without operator action — ensuring the hardwired trip function achieves complete shutdown. | 2026-03-26T01:43:08.656Z
SYS-REQ-010 | SUB-REQ-006 | derives | Hardwired trip function decomposed from system trip requirement | SUB-REQ-006 directly implements the high coolant temperature trip function mandated by SYS-REQ-010, specifying the 90°C cylinder head outlet trip setpoint with 2-second actuation, derived from OEM thermal limits and IEC 60034 protection requirements. | 2026-03-26T01:43:07.992Z
SYS-REQ-010 | SUB-REQ-005 | derives | Hardwired trip function decomposed from system trip requirement | SUB-REQ-005 directly implements the low lubricating oil pressure trip function mandated by SYS-REQ-010, specifying the 2.0 bar trip setpoint and 2-second actuation time at the main oil gallery, with pre-trip annunciation at 2.5 bar. | 2026-03-26T01:43:07.321Z
SYS-REQ-010 | SUB-REQ-004 | derives | Hardwired trip function decomposed from system trip requirement | SUB-REQ-004 directly implements the overspeed trip function required by SYS-REQ-010, specifying the 115% rated speed setpoint (863 rpm) and 1-second trip actuation time for the fuel rack, independent of digital control. | 2026-03-26T01:43:06.617Z
SYS-REQ-005 | SUB-REQ-003 | derives | Engine endurance from 24-hour mission reliability | SYS-REQ-005 requires 24h mission reliability of 0.999. SUB-REQ-003 translates this into 720h between-overhaul endurance providing the statistical basis. | 2026-03-26T01:43:05.901Z
SYS-REQ-006 | SUB-REQ-002 | derives | Engine speed tolerance from frequency requirement | SYS-REQ-006 requires 50 Hz ±2%; SUB-REQ-002 allocates the speed budget to the engine assembly. | 2026-03-26T01:43:05.208Z
SYS-REQ-001 | SUB-REQ-001 | derives | DUPLICATE of link-1774489349041 (SYS-001→SUB-001 engine start budget) | Flagged as duplicate during QC session 580; delete when API supports | 2026-03-26T01:42:55.041Z
SYS-REQ-005 | SUB-REQ-003 | derives | DUPLICATE of link-1774489385901 (SYS-005→SUB-003 engine endurance) | Flagged as duplicate during QC session 580; delete when API supports | 2026-03-26T01:42:30.384Z
SYS-REQ-006 | SUB-REQ-002 | derives | DUPLICATE of link-1774489385208 (SYS-006→SUB-002 engine speed) | Flagged as duplicate during QC session 580; delete when API supports | 2026-03-26T01:42:29.732Z
SYS-REQ-001 | SUB-REQ-001 | derives | Engine start self-sustain budget derives from system 10-second start requirement | SYS-REQ-001 requires rated output within 10 seconds. SUB-REQ-001 allocates the engine's 3-second contribution to self-sustaining combustion — this child exists to bound start air/ignition performance. | 2026-03-26T01:42:29.041Z
STK-REQ-001 | SYS-REQ-001 | derives | Operator monitoring need drives start sequence performance specification | STK-REQ-001 requires real-time operator display of EDG status; SYS-REQ-001 defines the 10-second start-to-rated-voltage performance that drives the most critical display parameters — breach of this threshold triggers control room alarms. | 2026-03-26T01:06:23.640Z
STK-REQ-004 | SYS-REQ-014 | derives | LCO support need derives single-train full-load capability | Shift supervisor must manage LCO — this requires confidence that one train carries full safety load during the allowed outage time | 2026-03-26T01:06:23.602Z
STK-REQ-003 | SYS-REQ-002 | derives | Alarm annunciation need derives automatic LOOP detection and start | Operator needs to know EDG status immediately — automatic start on LOOP is the precondition for meaningful alarm annunciation | 2026-03-26T01:06:23.576Z
STK-REQ-012 | SYS-REQ-005 | derives | Licensee reliability target derives 24-hour mission reliability requirement | The 0.999 mission reliability quantifies the licensee's need for sustained operation during extended LOOP | 2026-03-26T01:06:22.393Z
STK-REQ-010 | SYS-REQ-007 | derives | ONR SAP compliance derives dual-train redundancy with single failure criterion | SAP EKP.3 requires demonstration that no single failure defeats the safety function — dual independent trains satisfy this | 2026-03-26T01:06:22.392Z
STK-REQ-015 | SYS-REQ-015 | derives | Community expectation of accident prevention derives diverse AC source for SBO | Defence-in-depth beyond dual EDGs: if common cause defeats both EDGs, a diverse mobile source prevents core damage | 2026-03-26T01:06:22.389Z

## Linksets
Source Document | Target Document | Default Link Type | Link Count
system-requirements | architecture-decisions |  | 8
subsystem-requirements | verification-requirements |  | 56
interface-requirements | verification-requirements |  | 29
system-requirements | verification-requirements |  | 0
system-requirements | subsystem-requirements |  | 59
system-requirements | interface-requirements |  | 19
stakeholder-requirements | system-requirements |  | 23

## Sections
Document | Section | Short Code | Order | Requirements
architecture-decisions | Architecture Decisions | ARC | 0 | 8
interface-requirements | Interface Requirements | IFC | 0 | 28
stakeholder-requirements | Stakeholder Requirements | STK | 0 | 18
subsystem-requirements | Subsystem Requirements | SUB | 0 | 61
system-requirements | System Requirements | SYS | 0 | 15
verification-requirements | Verification Requirements | VER | 0 | 59