## Documents
Slug | Name | Short Code | Sections | Requirements | Created
architecture-decisions | Architecture Decisions | ARC | 1 | 11 | 2026-03-25T09:51:09.283Z
interface-requirements | Interface Requirements | IFC | 1 | 20 | 2026-03-25T09:51:08.993Z
stakeholder-requirements | Stakeholder Requirements | STK | 1 | 13 | 2026-03-25T09:51:08.374Z
subsystem-requirements | Subsystem Requirements | SUB | 1 | 63 | 2026-03-25T09:51:09.148Z
system-requirements | System Requirements | SYS | 1 | 29 | 2026-03-25T09:51:08.840Z
verification-requirements | Verification Requirements | VER | 1 | 109 | 2026-03-25T09:51:09.431Z

## Requirements
Ref | Text | Document | Section | Pattern | Verification | QA Score | Compliance | Rationale | Tags
ARC-REQ-001 | The PAT Subsystem SHALL comprise three sensor instruments (NIR spectrometer, Raman spectrometer, Laser Diffraction Analyser) connected to a centralised DAC Workstation, sustaining real-time CQA monitoring with any two instruments operational when one fails. | architecture-decisions | Architecture Decisions |  | Inspection | 100 |  | Three-instrument PAT architecture selected over single-sensor design to enable degraded-mode operation (SIL-3 H-004 mitigation). Updated with SHALL keyword per validation session 566 to correct architecture decision record format. | reqs-eng-session-566
ARC-REQ-002 | The Manufacturing Execution System SHALL comprise five functional modules: Electronic Batch Record Engine, Recipe Management, In-Process Control, Equipment Lifecycle Management, and Material Tracking, communicating via a GAMP 5 Category 4 qualified internal event bus. | architecture-decisions | Architecture Decisions |  | Inspection | 100 |  | Five-module MES architecture selected to align with 21 CFR Part 11 compliance domains and GAMP 5 (Good Automated Manufacturing Practice) categorisation. Updated with SHALL keyword per validation session 566 to correct architecture decision record format. | reqs-eng-session-566
ARC-REQ-003 | The Granulation and Blending Subsystem SHALL implement a linear single-train process sequence: High Shear Granulator, Granule Transfer System, Fluid Bed Dryer, Granule Sizing Mill, and IBC Blender, in that order without parallel processing paths. | architecture-decisions | Architecture Decisions |  | Inspection | 100 |  | Linear single-train topology minimises inter-vessel transfer complexity and OEB containment breaches. Updated with SHALL keyword per validation session 566 to correct architecture decision record format. | reqs-eng-session-566
ARC-REQ-004 | The Tablet Compression Subsystem SHALL comprise four components: Rotary Tablet Press operating at 20–80 RPM with per-station punch force monitoring, IPC Sampling Station, Metal Detection Unit, and Tablet Diversion Gate controlled by the PAT Subsystem and MES. | architecture-decisions | Architecture Decisions |  | Inspection | 86 |  | Four-component architecture provides complete in-process surveillance. The Metal Detection Unit and Tablet Diversion Gate are safety-critical components for H-004 mitigation. Updated with SHALL keyword per validation session 566 to correct architecture decision record format. | reqs-eng-session-566
ARC-REQ-005 | The Manufacturing Execution System SHALL be deployed on a dedicated redundant server pair (active-passive) housed in the plant's Grade C server room, with each server providing a minimum of 8 CPU cores, 32 GB RAM, and 2 TB RAID-6 storage, dimensioned to host all MES application components and support concurrent access by 20 users. | architecture-decisions | Architecture Decisions |  | Test | 86 |  | MES physical server infrastructure is a constraint derived from system performance (concurrent users, EBR throughput) and pharmaceutical GMP requirements for dedicated IT environments. The redundant pair ensures SIL-2 availability for the EBR and LOTO safety functions (H-006, H-007). Physical embodiment requirement resolves ontological mismatch between software classification and physical installation constraints. | session-565, mes, physical-embodiment, lint-fix-lh1, idempotency:ses565-mes-physical-server-infra, idempotency:ses565-mes-physical-server-infra
ARC-REQ-006 | The Manufacturing Execution System SHALL be validated as ISPE GAMP 5 Category 4 software, with no biological components, no interaction with biological materials or organisms, and no requirement for biocompatibility or sterilisation certification; all MES hardware and software components SHALL be validated for pharmaceutical manufacturing environments per FDA 21 CFR Part 11 and EU GMP Annex 11 only. | architecture-decisions | Architecture Decisions |  | Inspection | 86 |  | An explicit statement that the MES is Category 4 software with no biological embodiment is required to prevent misclassification in regulatory submissions and risk assessments. The MES interfaces with biological manufacturing processes but is not itself a biological system; this requirement establishes the validation category and confirms that biological safety regulations (ISO 10993) do not apply to MES components. | session-565, mes, gamp5, non-biological, lint-fix-lh5, idempotency:ses565-mes-gamp5-non-biological, idempotency:ses565-mes-gamp5-non-biological
ARC-REQ-007 | The process control system SHALL be powered from a dedicated 24 VDC industrial power supply rated at 1000 W with ±1% voltage regulation, protected by an online double-conversion UPS providing 30 minutes autonomy at full PLC load, and shall monitor supply voltage continuously, triggering a panel alarm if supply drops below 23.0 VDC or rises above 25.0 VDC. | architecture-decisions | Architecture Decisions |  | Test | 86 |  | The process control system's PLCs and safety I/O are safety-critical components (SIL-2, H-007 LOTO enforcement). A defined power supply specification and UPS backup are required to ensure continued interlocking function during mains power disturbances. The 24 VDC 1000 W specification is typical for mid-size PLC installations supporting 64 I/O modules and safety relay outputs. Voltage monitoring prevents silent hardware faults. | session-565, process-control-system, power, ups, lint-fix, idempotency:ses565-pcs-power-explicit, idempotency:ses565-pcs-power-explicit
ARC-REQ-010 | ARC: Material Handling and Dispensing — The material handling function is separated from granulation because it operates in a distinct cleanroom zone (ISO 7 weigh booth with laminar flow), has a different contamination control strategy (lot segregation, cleaning between materials vs. in-process cleaning between batches), and interfaces with ERP for material identity verification. Alternative considered: combining dispensing with granulation as a single feed-to-granulate train. Rejected because dispensing serves multiple downstream processes in multi-product facilities and has independent regulatory audit requirements (material traceability per EU GMP Annex 11). | architecture-decisions | Architecture Decisions |  | Inspection |  |  | Material handling and dispensing is architecturally separated from granulation because it operates under a distinct contamination control regime: ISO 7-classified weigh booth with laminar flow, lot segregation between materials, and independent regulatory audit trail per EU GMP Annex 11. Combining dispensing with granulation would collapse two independent failure domains (material identity error vs. in-process granulation failure) into one subsystem, increasing consequence of a single point failure. | architecture, material-handling, session-2, idempotency:arc-material-handling-2, informational
ARC-REQ-011 | ARC: Film Coating — The coating function is separated from compression because it operates a fundamentally different process (thermal spray-coating vs. mechanical forming), uses distinct equipment (perforated pan coater vs. rotary press), and has independent failure modes (spray nozzle blockage, coating uniformity) unrelated to compression quality. Alternative considered: integrating coating as a post-compression stage within the tablet compression subsystem. Rejected because coating operates at different throughput rates (45-minute batch cycle vs. continuous compression), requires separate air handling with solvent exhaust, and is optional for some products (uncoated tablets bypass this subsystem entirely). | architecture-decisions | Architecture Decisions |  | Inspection |  |  | Film coating is architecturally separated from tablet compression because the two functions occupy different process domains: thermal spray-coating in a perforated pan coater versus high-speed mechanical forming in a rotary press. Their failure modes are independent (nozzle blockage, coating non-uniformity vs. punch breakage, tooling wear), they operate at incompatible throughput rates (45-minute batch cycle vs. continuous compression), and coating is optional for some products — uncoated tablets bypass the subsystem entirely. Merging them would create an unnecessary operational dependency and a more complex failure analysis. | architecture, film-coating, session-2, idempotency:arc-film-coating-2, informational
ARC-REQ-012 | ARC: Packaging and Serialisation — Packaging and serialisation are combined into a single subsystem because they operate on the same physical line (blister forming, inspection, serialisation, aggregation are sequential stations on one conveyor), share a common data chain (serial number generation through to EPCIS upload), and are jointly regulated under EU FMD (Delegated Regulation 2016/161) and US DSCSA. Alternative considered: separating serialisation as a standalone IT subsystem. Rejected because the serialisation data flow is tightly coupled to physical packaging events (each blister sealed triggers serial number application), and separating them creates an interface complexity that adds failure modes without reducing coupling. | architecture-decisions | Architecture Decisions |  | Inspection |  |  | Packaging and serialisation are combined into a single subsystem because physical packaging events (blister sealing) and serialisation data events (serial number application) are causally coupled at every station — separating them would require a cross-subsystem interface at the point of highest coupling, adding failure modes without reducing interdependency. EU FMD Delegated Regulation 2016/161 (Falsified Medicines Directive) and US DSCSA jointly regulate the combined function, making a unified compliance boundary architecturally appropriate. | architecture, packaging, session-2, idempotency:arc-packaging-serial-2, informational
ARC-REQ-013 | ARC: Containment and Environmental Control — Environmental monitoring (HVAC, cleanroom) and containment (potent compound isolation, E-stop, machine safety) are combined because they share a common safety PLC, building utilities interface (air handling, pressure control), and SIL 2 safety integrity requirement. Their failure modes are correlated — loss of HVAC compromises both cleanroom classification and containment pressure cascade. Alternative considered: separating containment (safety function) from HVAC (environmental function). Rejected because the containment strategy depends on HVAC pressure cascade control — a containment breach response (switch to 100% exhaust) is an HVAC operating mode, not a separate system. Splitting them creates a dangerous interface where a containment alarm must command HVAC changes across a subsystem boundary. | architecture-decisions | Architecture Decisions |  | Inspection |  |  | Containment (potent compound isolation, E-stop, machine safety) and environmental monitoring (HVAC, cleanroom) are combined because their failure modes are causally correlated: loss of HVAC directly compromises containment pressure cascade, and the containment breach response (switch to 100% exhaust) is implemented as an HVAC operating mode. Separating them would place a SIL-2 safety function (containment breach response) across a subsystem interface, creating a cross-boundary command latency risk. A shared safety PLC governs both functions, making a single combined subsystem the safer and simpler architecture. | architecture, containment, environmental, session-2, idempotency:arc-containment-env-2, informational
IFC-REQ-001 | The interface between the Process Analytical Technology Subsystem and the Manufacturing Execution System SHALL transmit CQA limit exceedance alarms as structured OPC UA event notifications containing sensor ID, CQA parameter name, measured value, limit value, and timestamp, with end-to-end latency not exceeding 500 milliseconds. | interface-requirements | Interface Requirements |  | Test | 86 |  | H-004 drives SIL 3 on the CQA diversion path. The 500ms latency budget is derived from SYS-016's 2-second diversion actuation window: 500ms for PAT-to-MES signalling leaves 1500ms for MES processing, EBR annotation, and valve actuation command. OPC UA is mandated by ISA-95 for MES-to-process integration and provides built-in event semantics. | interface, pat, mes, sil-3, cqa-diversion, session-547, idempotency:ifc-pat-mes-cqa-alarm-547
IFC-REQ-002 | The Process Analytical Technology Subsystem SHALL publish sensor health status to the Manufacturing Execution System via OPC UA monitored items at 10-second intervals (±1 second tolerance), including signal-to-noise ratio, calibration deviation percentage, and operational state (nominal/degraded/failed) for each PAT sensor; in degraded state, SNR SHALL be reported as an absolute value (minimum detectable: SNR < 3.0 triggers 'failed' state) and calibration deviation SHALL be reported in percentage drift from last reference standard (>3.0% drift triggers 'degraded' state). | interface-requirements | Interface Requirements |  | Test | 86 |  | SYS-022 requires degraded-mode switching within 30 seconds of sensor degradation. A 10-second health reporting interval gives MES three data points before the 30-second deadline. The SNR threshold (< 3.0) and calibration deviation threshold (>3.0% drift) are derived from the PAT Sensor Drift scenario and validated instrument qualification parameters. These thresholds make the 'degraded' and 'failed' state transitions testable — pass criterion for IFC qualification tests requires demonstrated state changes at the defined thresholds. Added quantified criteria per validation session 566. | interface, pat, mes, sensor-health, session-547, idempotency:ifc-pat-mes-sensor-health-547
IFC-REQ-003 | The Manufacturing Execution System SHALL transmit diversion acknowledgment and operating mode commands to the Process Analytical Technology Subsystem via OPC UA method calls, confirming EBR annotation of each CQA diversion event within 1 second and commanding PAT mode transitions (nominal/degraded/calibration) with response confirmation. | interface-requirements | Interface Requirements |  | Test | 86 |  | Bidirectional handshake ensures the EBR records every diversion event before PAT resets its alarm state. The 1-second acknowledgment window is the MES share of the 2-second total diversion budget from SYS-016. Mode commands from MES ensure PAT does not autonomously resume real-time release after sensor degradation without MES-verified recalibration, critical for H-004 mitigation. | interface, pat, mes, cqa-diversion, sil-3, session-547, idempotency:ifc-mes-pat-diversion-ack-547
IFC-REQ-004 | The Process Analytical Technology Subsystem SHALL stream CQA measurement results to the Manufacturing Execution System at 30-second intervals via OPC UA data subscriptions, with each measurement record containing batch ID, equipment ID, timestamp, CQA parameter values (content uniformity, blend homogeneity, particle size distribution), model version, and confidence score. | interface-requirements | Interface Requirements |  | Test | 86 |  | SYS-020 requires full batch genealogy linking finished product to process parameter logs. Model version and confidence score are essential for post-hoc investigation when H-004 occurs, enabling root cause analysis to determine whether an OOS release resulted from model error versus process excursion. 30-second interval aligns with SYS-016 PAT acquisition rate. | interface, pat, mes, batch-genealogy, session-547, idempotency:ifc-pat-mes-cqa-data-547
IFC-REQ-005 | When the Manufacturing Execution System transitions the production line to degraded mode, the MES SHALL issue a manual sampling schedule command to the Process Analytical Technology Subsystem specifying 15-minute sampling intervals, sample point locations, and CQA parameters to test offline within 30 seconds of mode transition; SHALL receive sample submission confirmations from PAT within 120 seconds of each scheduled sample time; and SHALL generate a deviation record if any sample submission is not confirmed within 120 seconds of its scheduled time. | interface-requirements | Interface Requirements |  | Test | 86 |  | SYS-022 specifies manual in-process testing every 15 minutes during sensor-degraded mode. The 30-second command issuance deadline ensures the first manual sample is scheduled before the PAT monitoring gap exceeds the first 15-minute interval. The 120-second sample submission confirmation window accommodates laboratory analysis time and is the maximum acceptable lag before operator intervention is triggered. Both thresholds are measurable acceptance criteria for degraded-mode qualification. Explicit performance thresholds added per validation session 566 to resolve ambiguousReqs blocker. | interface, degraded-mode, superseded-by-session-554, superseded-by:IFC-REQ-009
IFC-REQ-006 | The interface between the Granulation and Blending Subsystem and the Process Analytical Technology Subsystem SHALL provide real-time NIR spectral data to the PAT DAC Workstation at maximum 30-second intervals for both the Fluid Bed Dryer in-line LOD probe (900-1700 nm, 2 nm resolution) and the IBC Blender in-vessel NIR probe (900-1700 nm, 4 nm resolution), with latency less than 5 seconds from acquisition to CQA model evaluation result. | interface-requirements | Interface Requirements |  | Test | 86 |  | The 30-second maximum interval and 5-second latency are derived from REQ-SEPHARMAMANUFACTURING-016 (30-second minimum PAT sample interval). The G&B-to-PAT spectral interface must meet this timing because both LOD endpoint and blend endpoint decisions are safety-quality decisions: a delayed LOD result could allow an under-dried batch to proceed to sizing, degrading PSD and tablet compressibility. | interface, granulation-blending, session-549, idempotency:ifc-gb-pat-nir-549
IFC-REQ-007 | The interface between the Manufacturing Execution System and the Granulation and Blending Subsystem SHALL transmit recipe setpoints (temperature, RPM, time, LOD target) to each equipment PLC within 2 seconds of step initiation, and SHALL receive process data feedback (CPP actual values, mass readings, alarm states) from the G&B subsystem at 10-second intervals for EBR recording. | interface-requirements | Interface Requirements |  | Test | 86 |  | The 2-second setpoint delivery latency ensures equipment reaches setpoint before material processing begins — derived from the slowest PLC scan cycle (500ms) plus up to 3 MES polling retries. The 10-second EBR feedback interval is the minimum required for regulatory compliance (FDA 21 CFR Part 11) to reconstruct process conditions during a deviations investigation — coarser intervals would prevent reconstruction of CPP excursions shorter than one interval. | interface, granulation-blending, session-549, idempotency:ifc-mes-gb-recipe-549
IFC-REQ-008 | The interface between the Granulation and Blending Subsystem and the Tablet Compression Subsystem SHALL transfer blended granules in a sealed IBC with a tamper-evident seal applied by MES-controlled automated sealing station, with the IBC mass and blend-complete authorisation code recorded in the batch genealogy before transfer is permitted. | interface-requirements | Interface Requirements |  | Inspection | 86 |  | The sealed IBC handoff at G&B-to-compression boundary is the primary batch integrity control point. MES-controlled sealing prevents manual opening or material substitution between blend completion and tablet press charging. The authorisation code links the specific IBC to its blend record, satisfying REQ-020 (batch genealogy) and enabling identification of compression batches affected if an upstream blend deviation is discovered during QC review. | interface, granulation-blending, session-549, idempotency:ifc-gb-compression-handoff-549
IFC-REQ-009 | When the Manufacturing Execution System transitions the production line to degraded mode, the MES SHALL issue a manual sampling schedule command to the Process Analytical Technology Subsystem within 30 seconds of mode transition, specifying 15-minute sampling intervals, at minimum 3 CQA parameters (API assay, blend uniformity, moisture content), and all required sample point locations. The MES SHALL receive and EBR-record PAT sample submission confirmations within 5 minutes of each scheduled sampling event; if a confirmation is not received within 5 minutes, the MES SHALL generate a critical alert and log a non-conformance event. | interface-requirements | Interface Requirements |  | Test | 86 |  | Derived from IFC-REQ-005. The 30-second command delivery window prevents manual sampling gaps when the PAT system transitions to degraded mode mid-batch. The 5-minute confirmation window is the maximum acceptable sampling latency before a non-conformance event must be logged under 21 CFR 211.192 (batch production records). The minimum 3-CQA-parameter floor ensures that API assay, blend uniformity, and moisture are never deferred, as these are the three attributes that determine batch release or rejection. | interface, degraded-mode, mes, pat-subsystem, session-554, supersedes:IFC-REQ-005, idempotency:ifc-mes-degraded-mode-quantified-554
IFC-REQ-010 | The interface between the Tablet In-Process Control System and the Process Analytical Technology Subsystem SHALL transmit individual tablet weight, hardness, and thickness measurements via OPC-UA at a minimum rate of one dataset per sampled tablet (minimum 2 Hz at 120 RPM with every-30th sampling), with timestamp synchronised to UTC ±1 s. | interface-requirements | Interface Requirements |  | Test | 86 |  | The PAT CQA model engine uses IPC data combined with NIR content uniformity to generate composite CQA predictions. Time synchronisation to UTC ±1 s is required to correlate IPC tablet weight with the NIR spectral acquisition window — a NIR scan lasts 30 s and covers ~3,600 tablets at 120 RPM; a 1 s timestamp error spans ~120 tablets, acceptable for the correlation model. | session-556, idempotency:ifc-tc-ipc-pat-556
IFC-REQ-011 | The interface between the Tablet Compression Subsystem and the Manufacturing Execution System SHALL write all in-process tablet rejection events (timestamp, station number, force value, reject reason) to the electronic batch record within 10 seconds of the rejection event, and SHALL write a subsystem status change (normal/degraded/stopped) to the MES within 5 seconds of the state transition. | interface-requirements | Interface Requirements |  | Test | 86 |  | 21 CFR Part 11 requires complete electronic batch records with no gaps; individual rejection events must be recorded because each rejected tablet represents an attributed product loss that the batch genealogy must account for. The 10-second write latency is a practical limit derived from MES database write performance at high-throughput compression (up to 500 rejections/min at 5% rejection rate); longer would risk buffer overflow and data loss. | session-556, idempotency:ifc-tc-mes-ebr-556
IFC-REQ-012 | The interface between the Film Coating Subsystem and the Manufacturing Execution System SHALL transmit coating recipe parameters (pan speed, inlet temperature, spray rate, atomisation pressure, target weight gain) from the MES to the coating subsystem and return in-process coating parameters (actual inlet/outlet temperature, spray rate, tablet weight gain) and batch disposition decisions to the MES at a minimum 30-second update interval, with all data writes to the Electronic Batch Record completed within 60 seconds of measurement. | interface-requirements | Interface Requirements |  | Test | 86 |  | Film coating is a GMP-controlled operation under 21 CFR Part 211 (Current Good Manufacturing Practice for Finished Pharmaceuticals); recipe execution parameters and in-process measurements are mandatory EBR entries. The 30-second update interval matches the coating process dynamics (pan rotation period ~10–20 seconds) and ensures that any excursion from coating weight target is captured within one control cycle before batch rejection criteria are exceeded. | session-558, qc, film-coating, mes, idempotency:ifc-012-film-coating-mes-v1
IFC-REQ-013 | The interface between the Tablet Compression Subsystem and the Film Coating Subsystem SHALL transfer compressed tablet cores via a closed IBC transfer system, with the Tablet Compression Subsystem providing a signed transfer record (batch ID, weight, tablet count, core hardness mean ± 3σ, friability result) to the Film Coating Subsystem before any coating operation commences; the Film Coating Subsystem SHALL reject the transfer if any core attribute falls outside the predefined acceptance range defined in the batch record. | interface-requirements | Interface Requirements |  | Inspection | 86 |  | Physical hand-off between compression and coating is a critical GMP in-process release step under 21 CFR Part 211.110 (Sampling and testing of in-process materials). Core quality attributes (hardness, friability) directly determine coating adhesion and film integrity; out-of-specification cores entering the coater cause coating defects that are difficult to detect without destructive testing post-coating. A signed transfer record with a defined rejection gate prevents downstream waste and protects batch integrity. | session-558, qc, tablet-compression, film-coating, idempotency:ifc-013-compression-coating-v1
IFC-REQ-014 | The interface between the Packaging and Serialisation Subsystem and the Manufacturing Execution System SHALL receive batch release authorisation and serialisation master data (product code, batch number, expiry date, GTIN) from the MES prior to line start, and SHALL return completed pack-level and case-level serial number aggregation records to the MES within 5 minutes of line clearance, with 100% serial number reconciliation enforced before the MES records batch disposition as complete. | interface-requirements | Interface Requirements |  | Test | 86 |  | EU Falsified Medicines Directive (FMD) Delegated Regulation 2016/161 and US Drug Supply Chain Security Act (DSCSA) mandate unique serialisation of every saleable unit and full aggregation to case and pallet level. The MES is the system of record for batch disposition; packaging cannot begin without MES authorisation (GMP two-person batch release) and the EBR cannot be closed without confirmed serial number reconciliation. The 5-minute reconciliation window is determined by regulatory serialisation verification system response time SLAs. | session-558, qc, packaging, mes, serialisation, idempotency:ifc-014-packaging-mes-v1
IFC-REQ-015 | The interface between the Film Coating Subsystem and the Packaging and Serialisation Subsystem SHALL transfer coated tablets via a closed IBC or chute system, with the Film Coating Subsystem providing a signed in-process release record (coating weight gain mean ± 2σ, dissolution test result if performed, appearance inspection result) to the Packaging Subsystem before any packaging operation commences; the Packaging Subsystem SHALL block line start and alert the MES if the release record is absent or indicates an out-of-specification attribute. | interface-requirements | Interface Requirements |  | Inspection | 86 |  | Coated tablets are the final intermediate product before primary packaging; coating weight gain and dissolution performance are Critical Quality Attributes per ICH Q8 (Pharmaceutical Development) and must be within specification before patients could be exposed to the dosage form. A hard interlock preventing packaging without a valid release record eliminates the GMP deviation risk of packaging non-conforming tablets, which would require a costly and time-consuming recall. | session-558, qc, film-coating, packaging, idempotency:ifc-015-coating-packaging-v1
IFC-REQ-016 | The interface between the Containment and Environmental Control Subsystem and the Manufacturing Execution System SHALL transmit classified area environmental parameters (temperature, relative humidity, differential pressure, particle counts at ≥0.5 µm and ≥5 µm) to the MES at a minimum 5-minute update interval; when any parameter exceeds the action limit defined in the Site Master File, the MES SHALL halt all affected manufacturing operations and record an environmental deviation event in the Electronic Batch Record within 30 seconds of alarm receipt. | interface-requirements | Interface Requirements |  | Test | 86 |  | GMP cleanroom environments under EU GMP Annex 1 (Manufacture of Sterile Medicinal Products) and ISO 14644-1 (Cleanrooms and associated controlled environments) require continuous environmental monitoring with documented response to excursions. For OEB 4/5 potent compound areas (OEL < 1 µg/m³), pressure differential loss is a safety-critical event: a positive-pressure failure allows potent aerosol escape to adjacent areas. The 30-second MES halt window is set to prevent more than one in-process tablet unit from being produced in an unmonitored environment. | session-558, qc, containment, mes, environmental, idempotency:ifc-016-containment-mes-v1
IFC-REQ-017 | The interface between the Material Handling and Dispensing Subsystem and the Manufacturing Execution System SHALL receive dispensing orders (material code, lot number, target weight, tolerance ±0.1%) from the MES and SHALL return verified dispensing records (material identity confirmed by NIR verification, actual dispensed weight, operator ID, balance calibration status) to the MES within 60 seconds of each weighing operation; the MES SHALL reject any dispensing record where the actual weight deviates from target by more than ±0.5% and record a GMP deviation event. | interface-requirements | Interface Requirements |  | Test | 86 |  | Dispensing is the first in-process step in oral solid dosage manufacturing and the point of highest risk for API content non-uniformity. EU GMP Part II (API manufacturing) and 21 CFR Part 211.101 (Charge-in of components) require documented verification of material identity and weight for every dispensing event. A ±0.1% target tolerance with ±0.5% rejection threshold provides a two-sigma safety margin against dosage uniformity failure while remaining achievable by calibrated pharmaceutical balance equipment (typical METTLER-TOLEDO ICS balance accuracy ±0.02%). | session-558, qc, material-handling, mes, dispensing, idempotency:ifc-017-material-handling-mes-v1
IFC-REQ-018 | The interface between the Material Handling and Dispensing Subsystem and the Granulation and Blending Subsystem SHALL physically transfer dispensed and verified raw material containers (IBCs, drums, sacks) to the granulator charge point using a documented, barcode-verified transfer protocol; the Granulation and Blending Subsystem SHALL perform a secondary identity verification scan of each container barcode against the dispensing record before allowing material to be charged into the high shear granulator, and SHALL reject and alert the MES if any container scan fails identity verification. | interface-requirements | Interface Requirements |  | Inspection | 86 |  | The physical handoff from dispensing to granulation is the last point at which a wrong material or wrong lot can be intercepted before it is irreversibly mixed into a granule batch. A double-verification protocol (dispensing NIR + granulation barcode scan) implements a two-barrier defence against mix-ups, which is a root-cause pattern in pharmaceutical recalls (FDA recall database analysis: ~12% of solid dosage form recalls involve wrong API or wrong excipient). Barcode verification at the charge point is low-cost relative to the cost of a contaminated batch recall (~0–50M). | session-558, qc, material-handling, granulation, idempotency:ifc-018-material-granulation-v1
IFC-REQ-019 | The interface between the Enterprise Resource Planning System and the Manufacturing Execution System SHALL deliver electronic production orders (product code, target batch size, BOM version, planned start date) from the ERP to the MES at least 24 hours before scheduled manufacturing start, and SHALL receive confirmed batch yield, actual cycle time, and material consumption quantities from the MES within 4 hours of batch completion; the MES SHALL not allow production to commence without a valid, ERP-issued production order reference in the Electronic Batch Record header. | interface-requirements | Interface Requirements |  | Test | 86 |  | GMP site operations under EU GMP Part I require that every manufacturing operation is performed against an authorised, documented production order. The ERP-to-MES production order handshake is the GMP-mandated control preventing unauthorised or unplanned manufacturing (an audit finding category). Batch yield and consumption data returned to ERP enable inventory reconciliation and release cost accounting. The 24-hour advance notice requirement allows the MES to stage material dispensing orders and equipment verification tasks within the current shift schedule. | session-558, qc, erp, mes, production-order, idempotency:ifc-019-erp-mes-v1
IFC-REQ-020 | The interface between the Laboratory Information Management System and the Manufacturing Execution System SHALL receive in-process and release sample requests generated by the MES (sample ID, sample point, test method, specification reference), and SHALL return analytical results (test method, result value with units, specification limits, pass/fail verdict, analyst ID, instrument ID) to the MES within the turnaround time specified in the master test schedule; the MES SHALL block batch disposition to 'released' status until all mandatory release test results are received from LIMS with a passing verdict. | interface-requirements | Interface Requirements |  | Test | 86 |  | GMP batch release under 21 CFR Part 211.165 and EU GMP Chapter 4 requires that all specified release tests are completed with documented results before a batch is released for distribution. LIMS is the system of record for analytical results; the MES is the system of record for batch disposition. The bi-directional interface ensures a closed-loop release workflow where sample chain of custody, analytical data, and batch status are maintained in separate validated systems with a defined integration point, reducing the risk of manual transcription errors that have historically driven pharmaceutical data integrity citations. | session-558, qc, lims, mes, batch-release, idempotency:ifc-020-lims-mes-v1
STK-REQ-001 | The manufacturing line SHALL achieve a minimum Overall Equipment Effectiveness (OEE) of 75% during Normal Production mode, measured over a rolling 30-day production period. | stakeholder-requirements | Stakeholder Requirements | ubiquitous | Test | 100 |  | Production Supervisor and Plant Manager stakeholder need: 75% OEE is the pharmaceutical industry minimum acceptable threshold for commercial viability; falling below this threshold jeopardises product supply continuity and plant economics. Derived from Normal Production Campaign scenario (300,000 tablets/day ibuprofen campaign). | idempotency:stk-pharma-oee-001
STK-REQ-002 | The manufacturing line SHALL maintain electronic batch records (EBRs) that fully comply with FDA 21 CFR Part 11 and EU Annex 11, providing a complete, unbroken audit trail for every production batch from material receipt to product release. | stakeholder-requirements | Stakeholder Requirements | ubiquitous | Inspection | 86 |  | FDA/EMA Regulatory Inspector stakeholder need: 21 CFR Part 11 and Annex 11 are mandatory legal requirements for electronic records in pharmaceutical manufacturing. An incomplete audit trail constitutes a critical GMP deficiency that can trigger a warning letter, consent decree, or product recall. Derived from Electronic batch record data integrity failure hazard. | idempotency:stk-pharma-ebr-002
STK-REQ-003 | The manufacturing line SHALL perform continuous real-time in-process quality monitoring using Process Analytical Technology (PAT) instruments, with automatic batch diversion when any critical quality attribute (CQA) exceeds its acceptance limit. | stakeholder-requirements | Stakeholder Requirements | ubiquitous | Test | 100 |  | QC Analyst stakeholder need: real-time PAT monitoring prevents out-of-specification product from reaching patients. Automatic diversion on CQA breach eliminates the latency of offline laboratory testing. Derived from Out-of-specification dosage form released to market hazard and PAT Sensor Drift Degraded Operation scenario. | idempotency:stk-pharma-pat-003
STK-REQ-004 | The manufacturing line SHALL maintain containment integrity for potent compounds with Occupational Exposure Limit (OEL) below 1 µg/m³, achieving an airborne concentration at operator breathing zone of less than 10% of OEL during all production, maintenance, and changeover operations. | stakeholder-requirements | Stakeholder Requirements | ubiquitous | Test | 86 |  | EHS Officer stakeholder need: potent compound airborne exposure is the primary occupational health risk in pharmaceutical manufacturing. MoP basis: OEB 1-5 classification scale is the industry-standard banding system defined in ISPE Risk-MaPP Baseline Guide and referenced in EMA (European Medicines Agency) Guideline on Setting Health Based Exposure Limits; OEL banding requires corresponding containment strategy per COSHH Regulation 7 engineering controls hierarchy. | reqs-eng-session-566
STK-REQ-005 | When an emergency condition is detected, the manufacturing line SHALL achieve a full controlled stop of all process equipment within 10 seconds, isolating energy sources and securing product-contact surfaces. | stakeholder-requirements | Stakeholder Requirements | event | Test | 100 |  | EHS Officer and Production Supervisor stakeholder need: 10-second emergency stop time is consistent with machinery safety directive EN ISO 13850 performance level requirements for pharmaceutical equipment in GMP environments. Slow emergency stop risks operator injury and product contamination. Derived from Emergency Stop mode and Tablet Press Mechanical Jam Failure scenario. | idempotency:stk-pharma-estop-005
STK-REQ-006 | The manufacturing line SHALL comply with EU GMP Annex 1 (for sterile areas if applicable), EU GMP Annex 15 (validation), FDA Guidance on Process Validation, and ICH Q10 pharmaceutical quality system requirements throughout its operational lifecycle. | stakeholder-requirements | Stakeholder Requirements | ubiquitous | Inspection | 86 |  | FDA/EMA Regulatory Inspector stakeholder need: compliance with GMP regulations is a legal prerequisite for product release; non-compliance results in regulatory action up to facility closure. Derived from Pharmaceutical regulatory compliance framework entity. | idempotency:stk-pharma-gmp-006
STK-REQ-007 | The manufacturing line SHALL support validated product changeover procedures that achieve cross-contamination residue levels below 10 ppm (API to API) or the toxicological threshold of 0.1% of minimum daily therapeutic dose of the previous product, whichever is lower. | stakeholder-requirements | Stakeholder Requirements | ubiquitous | Test | 86 |  | QC Analyst and Production Supervisor stakeholder need: cross-contamination limits are defined by MACO (Maximum Allowable Carry-Over) calculations per EMA cleaning validation guideline. Exceeding these limits causes drug product adulteration. Derived from Cross-contamination between drug products hazard and Product Changeover Cleaning Validation scenario. | idempotency:stk-pharma-changeover-007
STK-REQ-008 | The manufacturing line SHALL integrate with the external drug serialisation system to apply unique identifiers to 100% of saleable units and report serialisation data compliant with EU FMD (Delegated Regulation 2016/161) and US DSCSA (21 USC 360eee) within 24 hours of packaging completion. | stakeholder-requirements | Stakeholder Requirements | ubiquitous | Test | 86 |  | FDA/EMA Regulatory Inspector stakeholder need: serialization is a legal requirement for drug traceability and anti-counterfeiting. Failure to serialize 100% of units within 24 hours creates regulatory violations and prevents product distribution. Derived from Drug serialization and track-and-trace system external entity. | idempotency:stk-pharma-serial-008
STK-REQ-009 | When a non-critical equipment fault or PAT sensor degradation is detected, the manufacturing line SHALL maintain production capability at a minimum of 50% nominal throughput while operating under enhanced manual in-process testing protocols, until the fault is rectified. | stakeholder-requirements | Stakeholder Requirements | event | Test | 86 |  | Production Supervisor stakeholder need: partial production capability prevents complete supply chain disruption during minor equipment faults. 50% minimum throughput is the commercial viability threshold for continued manufacturing against urgent patient supply orders. Derived from Degraded Production mode and PAT Sensor Drift scenario. | idempotency:stk-pharma-degraded-009
STK-REQ-010 | The manufacturing line SHALL maintain bidirectional traceability of all raw materials, intermediates, and finished product, enabling complete batch genealogy reconstruction — identifying all equipment, operators, and materials involved in any given batch — within 4 hours of a recall investigation request. | stakeholder-requirements | Stakeholder Requirements | ubiquitous | Test | 86 |  | GMP Material Handler and Regulatory Inspector stakeholder need: bidirectional traceability is required by FDA 21 CFR 211.188 and EU GMP Chapter 4. The 4-hour reconstruction requirement aligns with FDA CDER recall assessment timelines; failure to produce genealogy delays field corrections and increases recall scope. | idempotency:stk-pharma-traceability-010
STK-REQ-011 | While operating in Normal Production mode, the manufacturing line SHALL maintain cleanroom conditions at ISO Class 7 (EU GMP Grade C, ≤352,000 particles ≥0.5µm/m³) with positive pressure differential of at least 15 Pa relative to adjacent unclassified areas. | stakeholder-requirements | Stakeholder Requirements | state | Test | 86 |  | QC Analyst and EHS Officer stakeholder need: ISO Class 7 is the minimum cleanroom classification required for tablet and capsule manufacturing under EU GMP. Positive pressure prevents particulate ingress. Loss of pressure differential is a critical GMP excursion requiring batch investigation. Derived from Cleanroom environmental control failure hazard. | idempotency:stk-pharma-cleanroom-011
STK-REQ-012 | The manufacturing line SHALL provide documented lockout/tagout (LOTO) procedures and physical isolation points for all energy sources on every equipment unit, achieving a machinery safety performance level of PLd per EN ISO 13849-1 for guard interlocking circuits. | stakeholder-requirements | Stakeholder Requirements | ubiquitous | Inspection | 86 |  | Equipment Maintenance Technician and EHS Officer stakeholder need: LOTO is required by OSHA 29 CFR 1910.147 and EU Machinery Directive 2006/42/EC. PLd is the minimum performance level for pharmaceutical equipment with medium frequency use and moderate injury severity. Derived from Tablet press mechanical entrapment hazard. | idempotency:stk-pharma-loto-012
STK-REQ-013 | The manufacturing line SHALL produce finished drug products that comply with pharmacopoeial specifications for tablet hardness, disintegration, dissolution, content uniformity (AV ≤ 15.0 for L1 per Ph.Eur./USP), and potency (98.0–102.0% label claim) for 100% of released batches. | stakeholder-requirements | Stakeholder Requirements | ubiquitous | Test | 86 |  | Patient stakeholder need: pharmacopoeial compliance directly ensures patient safety and therapeutic efficacy. AV ≤ 15.0 at Stage 1 and potency 98-102% are USP/Ph.Eur. release criteria; out-of-range product poses direct patient harm risk including under-dosing and over-dosing. This is the terminal quality gate for all manufactured product. | idempotency:stk-pharma-product-quality-013
SUB-REQ-001 | The PAT Subsystem NIR spectrometer SHALL acquire diffuse reflectance spectra (900-1700 nm, minimum 256 wavelength channels, 8 cm-1 resolution) at 30-second intervals from each monitored process point, with signal-to-noise ratio exceeding 5000:1 and automatic dark-current correction between acquisitions. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | NIR is the primary sensor for content uniformity and moisture monitoring. SYS-016 mandates 30-second acquisition. The 5000:1 SNR threshold is the minimum for reliable PLS chemometric model discrimination of API concentration within 2% RSD, derived from ICH Q2(R1) analytical method validation requirements. 8 cm-1 resolution matches pharmaceutical industry standard for solid dosage monitoring. | subsystem, pat, nir, sil-3, session-547, idempotency:sub-pat-nir-acquisition-547
SUB-REQ-002 | The PAT Subsystem Raman spectrometer SHALL acquire spectra (200-3200 cm-1, spectral resolution 4 cm-1) at 30-second intervals using a 785 nm excitation laser at power not exceeding 500 mW, with automatic fluorescence background subtraction and cosmic ray rejection. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Raman provides polymorphic form identification and API quantification complementary to NIR. SYS-016 mandates 30-second acquisition. 785 nm excitation is the standard for pharmaceutical applications, balancing fluorescence avoidance with Raman cross-section. 500 mW power limit prevents thermal degradation of heat-sensitive APIs. Fluorescence subtraction is essential for excipient-rich formulations. | subsystem, pat, raman, sil-3, session-547, idempotency:sub-pat-raman-acquisition-547
SUB-REQ-003 | The PAT Subsystem SHALL evaluate all CQA chemometric models (content uniformity PLS, blend homogeneity PCA, particle size correlation) within 5 seconds of sensor data acquisition, using cryptographically signed model files with version tracking, and SHALL reject any model file whose SHA-256 checksum does not match the validated model registry. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | SYS-016 mandates CQA model evaluation within 5 seconds. Model integrity is a direct H-004 mitigation: a corrupted or unauthorised model could approve OOS product for release. Cryptographic signing with SHA-256 verification ensures only validated models execute in production, meeting 21 CFR Part 11 requirements for computerised system validation. Version tracking enables post-incident root cause analysis. | subsystem, pat, cqa-model, sil-3, h-004, session-547, idempotency:sub-pat-cqa-model-eval-547
SUB-REQ-004 | When a CQA limit exceedance is detected, the PAT Subsystem SHALL actuate the batch diversion valve to the reject position within 2 seconds, confirm valve position via discrete feedback sensor, and maintain the diversion state until receiving an explicit MES acknowledgment and reset command. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | SYS-016 mandates 2-second diversion actuation. The valve position feedback sensor provides independent confirmation that the diversion physically occurred, critical for SIL 3 integrity of the H-004 mitigation. Latching in divert-state until MES acknowledgment prevents race conditions where PAT could reset before the EBR records the event, ensuring no diversion goes unrecorded. | subsystem, pat, diversion, sil-3, h-004, session-547, idempotency:sub-pat-diversion-valve-547
SUB-REQ-005 | The PAT Subsystem SHALL perform continuous sensor self-diagnostics evaluating signal-to-noise ratio, wavelength calibration accuracy (against internal reference standard), and detector dark-current stability, and SHALL declare sensor-degraded state within 15 seconds when any diagnostic parameter deviates beyond validated operating limits. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | SYS-022 requires degraded-mode transition within 30 seconds. The 15-second detection window allocates half the budget to PAT self-diagnosis and half to MES notification and mode switching. Internal reference standard calibration check (typically polystyrene for NIR, silicon for Raman) is the pharmaceutical industry standard per ASTM E1840. Without continuous self-diagnostics, calibration drift is the primary root cause pathway for H-004. | subsystem, pat, sensor-health, sil-3, h-004, session-547, idempotency:sub-pat-sensor-diagnostics-547
SUB-REQ-006 | While in sensor-degraded state, the PAT Subsystem SHALL suspend real-time CQA model evaluation on the affected sensor channel within 5 seconds of degradation detection, continue acquisition on unaffected channels at ≥70% of nominal per-channel CQA evaluation rate, present manual sampling prompts to operators at 15-minute intervals (±30 seconds) with sample identification barcodes, and record all manual sample submissions with timestamps for MES integration. The PAT Subsystem SHALL maintain a minimum of 1 unaffected sensor channel in active CQA evaluation throughout degraded-mode operation. | subsystem-requirements | Subsystem Requirements |  | Demonstration | 86 |  | SYS-022 mandates 15-minute manual sampling and 50% throughput maintenance during degraded mode. The 5-second suspension window closes the gap between degradation detection and alert issuance. The ≥70% per-channel evaluation rate on surviving channels ensures that a 3-channel PAT system can sustain meaningful CQA coverage on 2 channels. The ±30-second sampling prompt tolerance accommodates operator workflow without breaching the 15-minute GMPsampling requirement. Minimum 1 active channel requirement prevents total real-time monitoring blackout during multi-sensor degradation. Performance floors added per validation session 566. | pat-subsystem, degraded-mode, superseded-by-session-554, superseded-by:SUB-REQ-024
SUB-REQ-007 | The PAT Subsystem laser diffraction analyser SHALL measure particle size distribution (0.5-2000 micron range, D10/D50/D90 reporting) at 30-second intervals during granulation and blending stages, with measurement repeatability within 2% RSD on D50 for reference standard material. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | SYS-016 lists laser diffraction as a mandated PAT sensor. Particle size distribution is a critical quality attribute for tablet dissolution rate and content uniformity per ICH Q6A. The 2% RSD repeatability on D50 is the ISO 13320 acceptance criterion for pharmaceutical laser diffraction, ensuring the measurement is sufficiently precise to detect granule over-growth that would cause segregation and content uniformity failure. | subsystem, pat, laser-diffraction, session-547, idempotency:sub-pat-laser-diffraction-547
SUB-REQ-008 | The Manufacturing Execution System SHALL enforce 21 CFR Part 11 compliant electronic signatures on all EBR critical entries (batch release, deviation acknowledgment, in-process hold, parameter override), requiring biometric or two-factor authentication, with each signature binding the signer identity, date/time, and signing meaning to the record. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | SYS-015 mandates electronic signatures with access controls. FDA 21 CFR Part 11.50 requires that signed records clearly indicate the printed name, date/time, and meaning of the signature. Two-factor authentication exceeds the minimum Part 11 requirement but is standard practice after FDA warning letters citing weak e-signature controls. H-006 safe state includes system lockout for forensic investigation, making signature integrity the first line of defense. | subsystem, mes, part-11, sil-2, h-006, session-547, idempotency:sub-mes-esig-547
SUB-REQ-009 | The Manufacturing Execution System SHALL maintain a tamper-evident audit trail recording every EBR creation, modification, and deletion event, capturing the original value, new value, operator ID, workstation ID, timestamp (UTC, NTP-synchronised to within 100 ms), and operator-entered reason for change. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | 21 CFR Part 11.10(e) requires complete audit trails; SIL-2 H-006 mandate. Upgraded from Inspection to Test per IEC 61508 (Functional safety of E/E/PE safety-related systems) requirements for SIL-2 safety functions — audit trail completeness must be demonstrated by active test (injection of EBR events and verification of append-only log) not static inspection. Test verification aligns with the VER-REQ-019 which tests audit trail tamper resistance. | subsystem, mes, audit-trail, part-11, sil-2, h-006, session-547, idempotency:sub-mes-audit-trail-547
SUB-REQ-010 | The Manufacturing Execution System SHALL compute and store a SHA-256 cryptographic hash on every EBR write operation, maintain a hash chain linking consecutive writes, and SHALL detect and alert on any hash chain discontinuity within one EBR backup cycle (15 minutes maximum). | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | SYS-015 mandates cryptographic hash verification on every write. The hash chain (each hash includes the previous hash) provides tamper evidence stronger than individual hashes, detecting both modification and deletion of intermediate records. Detection within one backup cycle ensures that if H-006 occurs, the maximum exposure window before alert is 15 minutes, aligning with the SYS-015 backup interval. | subsystem, mes, data-integrity, sil-2, h-006, session-547, idempotency:sub-mes-crypto-integrity-547
SUB-REQ-011 | The Manufacturing Execution System SHALL maintain a real-time lockout registry mapping each equipment unit to its lockout state (locked/unlocked), lockout holder (operator ID), lock application timestamp, and lock type (maintenance/cleaning/calibration), and SHALL prevent any equipment start command while at least one active lockout is registered against that equipment. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | SYS-024 mandates electronic lockout verification preventing restart. The lockout registry is the single source of truth for equipment safety state, replacing or augmenting physical padlocks. H-007 (mechanical entrapment) requires that restart prevention is absolute, not advisory. Multiple lock types support concurrent lockout by different disciplines (maintenance LOTO plus cleaning hold), as required in pharmaceutical changeover where cleaning and maintenance overlap. | subsystem, mes, loto, sil-2, h-007, session-547, idempotency:sub-mes-loto-registry-547
SUB-REQ-012 | The Manufacturing Execution System SHALL log every LOTO event (lock application, lock removal, restart attempt while locked, override attempt) in the EBR with operator ID, equipment ID, timestamp, lock type, and event outcome (success/denied), retaining logs for the batch record retention period. | subsystem-requirements | Subsystem Requirements |  | Inspection | 86 |  | SYS-024 mandates logging all LOTO events with operator ID, timestamp, and equipment ID. Including restart-attempt-while-locked and override-attempt events provides forensic evidence for H-007 near-miss investigation. Retention for the batch record period (typically 1 year past expiry per 21 CFR 211.180) ensures LOTO records are available for regulatory inspection of any batch produced during the maintenance window. | subsystem, mes, loto, audit-trail, session-547, idempotency:sub-mes-loto-logging-547
SUB-REQ-013 | The Manufacturing Execution System SHALL record batch genealogy linking each production batch to raw material lot numbers (via barcode scan at dispensing), equipment IDs (via PLC integration), process parameter time-series (via historian interface), operator IDs (via e-signature at each stage), and PAT CQA results (via OPC UA subscription), enabling recall scope determination within 4 hours of query. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | SYS-020 mandates full batch genealogy with 4-hour recall scope determination. The 4-hour constraint drives the database query architecture: the genealogy must be queryable by any dimension (material lot, equipment, operator, date range) without full table scan. Barcode scan at dispensing is the GMP-standard method for material identity verification, eliminating transcription error that could make genealogy unreliable. | subsystem, mes, batch-genealogy, session-547, idempotency:sub-mes-batch-genealogy-547
SUB-REQ-014 | The Manufacturing Execution System SHALL perform automated EBR database backups at intervals not exceeding 15 minutes, with backup integrity verified by hash comparison, and SHALL restore from the most recent verified backup to a functional state within 30 minutes of a data integrity failure detection. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | SYS-015 mandates backup intervals not exceeding 15 minutes. The 30-minute recovery time objective ensures that H-006 safe state (switch to paper backup) does not persist longer than one production stage. Hash-verified backups prevent restoration of already-corrupted data, which would propagate the H-006 failure mode rather than recovering from it. | subsystem, mes, backup, sil-2, h-006, session-547, idempotency:sub-mes-ebr-backup-547
SUB-REQ-015 | When a data integrity failure is detected (hash chain discontinuity or backup verification failure), the Manufacturing Execution System SHALL switch to verified paper backup record mode within 60 seconds, generating pre-formatted paper batch record forms with the current batch context pre-populated, and SHALL lock the electronic system for forensic investigation. | subsystem-requirements | Subsystem Requirements |  | Demonstration | 86 |  | H-006 safe state mandates switch to verified paper backup and electronic system lockout. The 60-second switchover ensures no batch recording gap during the transition. Pre-populated paper forms reduce transcription error during the high-stress switchover event. System lockout for forensics preserves the evidence chain for the data integrity investigation required by FDA guidance on data integrity (2018). | subsystem, mes, paper-backup, sil-2, h-006, session-547, idempotency:sub-mes-paper-backup-547
SUB-REQ-016 | When the High Shear Granulator wet mass torque profile or integrated NIR wet-mass spectrum reaches the validated endpoint criterion, the Granulation and Blending Subsystem SHALL stop granulation within 10 seconds and initiate granule discharge transfer to the Fluid Bed Dryer. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Granulation endpoint detection is the primary process control point ensuring granule size and density are within specification. A 10-second stop-and-transfer limit prevents over-granulation (overwetting increases granule density, reducing tablet compressibility). The dual criterion (torque OR NIR) provides fallback if one sensor is unavailable per the PAT degraded-mode requirement (REQ-SEPHARMAMANUFACTURING-022). | subsystem, granulation-blending, session-549, sil-2, idempotency:sub-gb-hsg-endpoint-549
SUB-REQ-017 | The Fluid Bed Dryer SHALL reduce granule loss-on-drying (LOD) to the target value (product-specific, typically 1.0-3.0% w/w) plus or minus 0.5% w/w within the validated drying time window, as measured by the in-line NIR LOD probe at 60-second intervals. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | LOD at FBD discharge is a CQA because residual moisture directly affects tablet compressibility and chemical stability. Over-drying below 1.0% causes friable granules and poor compaction; under-drying above target increases risk of chemical degradation and sticky blend. The plus or minus 0.5% acceptance band is derived from ICH Q6A tablet dissolution specification tolerance and NIR LOD method validation precision (RSD less than 0.3%). | subsystem, granulation-blending, session-549, sil-2, idempotency:sub-gb-fbd-lod-549
SUB-REQ-018 | The Fluid Bed Dryer SHALL maintain inlet air temperature within plus or minus 2 degrees Celsius of the MES recipe setpoint throughout the drying cycle, and SHALL raise an alarm and suspend drying if the inlet air temperature deviates by more than 5 degrees Celsius for more than 60 seconds. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Inlet air temperature is a CPP affecting drying rate and product bed temperature. Exceedance beyond plus or minus 5 degrees Celsius risks thermal degradation of heat-sensitive APIs (stability shelf life driven by ICH Q1A). The 60-second tolerance window is derived from the thermal inertia of a 100L product bed — step changes propagate to the product bed within 90 seconds, giving 30 seconds of corrective action margin before product impact. | subsystem, granulation-blending, session-549, sil-2, idempotency:sub-gb-fbd-temp-549
SUB-REQ-019 | The Granule Sizing Mill SHALL reduce post-drying granule agglomerates such that the resulting sized granule D90 is less than 800 micrometres and D50 is between 200 and 600 micrometres, verified by off-line laser diffraction sampling within 15 minutes of mill discharge. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | PSD at sizing mill discharge is a CQA for tablet compression: coarse granules (D90 greater than 800 micrometres) cause tablet weight variation exceeding the REQ-SEPHARMAMANUFACTURING-025 plus or minus 5% rejection limit, and fine granules (D50 less than 200 micrometres) cause hopper segregation in the tablet press feed frame. The 15-minute off-line sampling window is the minimum required by stability and process validation protocols before blend step can proceed. | subsystem, granulation-blending, session-549, sil-2, idempotency:sub-gb-mill-psd-549
SUB-REQ-020 | The IBC Blender SHALL achieve a blend uniformity of API content RSD less than or equal to 5.0% across the blend mass, as measured by the in-IBC NIR probe at each of three blending speed setpoints (6 RPM, 10 RPM, 14 RPM) validated per ICH Q2(R1), before the MES issues blend-complete authorisation. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Blend uniformity RSD less than or equal to 5.0% is the USP Chapter 905 content uniformity acceptance criterion for tablets. NIR blend endpoint monitoring in the validated IBC geometry is required by the FDA Process Analytical Technology Guidance (2004) as an alternative to destructive sampling. Three-setpoint validation covers the RPM range across product viscosity variants — a single RPM setpoint would fail for high-viscosity batches where blending time increases non-linearly. | subsystem, granulation-blending, session-549, sil-2, idempotency:sub-gb-ibc-blend-endpoint-549
SUB-REQ-021 | The Granulation and Blending Subsystem SHALL record the mass of each material charge and transfer at each process step, and SHALL flag a mass balance error if the cumulative yield from raw material input to IBC discharge is outside the range 97.0% to 101.0% of theoretical batch yield. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Mass balance tracking from dispensed API weight through granulation, drying, sizing, and blend is a GMP regulatory requirement under 21 CFR 211.182 batch record content. The 97-101% window accounts for expected process losses (dust, sampling, vessel heel) while flagging uncontrolled losses that could indicate material mix-up, spill, or diversion. Values outside this range require investigation per SOPs before batch can proceed. | subsystem, granulation-blending, session-549, sil-2, idempotency:sub-gb-mass-balance-549
SUB-REQ-022 | When the PAT NIR blend-endpoint monitoring is unavailable (sensor fault or communication loss), the Granulation and Blending Subsystem SHALL continue IBC blending for the validated fixed-time blend duration specified in the MES recipe (minimum 20 minutes at validated RPM), require a supervisory operator authorisation before issuing blend-complete, and SHALL log the PAT-unavailable event in the EBR with timestamp and reason. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Degraded-mode performance floor is required per REQ-SEPHARMAMANUFACTURING-022. Fixed-time blending is the validated manual fallback when PAT NIR is unavailable — the 20-minute minimum time is the validated worst-case blend time from development studies. Supervisory authorisation provides a human check replacing the automated NIR endpoint. Without this requirement, PAT NIR failure would halt production with no recovery path, creating a safety-quality trade-off where operators bypass controls. | subsystem, granulation-blending, session-549, sil-2, idempotency:sub-gb-degraded-blend-549
SUB-REQ-023 | While processing OEB 3 or higher potency compounds (OEL less than 10 micrograms per cubic metre), the Granulation and Blending Subsystem SHALL maintain contained transfer operations at all inter-vessel transfer points, with airborne API concentration in the operator breathing zone not exceeding 1 microgram per cubic metre as verified by personal air sampling during qualification. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Containment requirement derives from REQ-SEPHARMAMANUFACTURING-004 (OEB containment integrity) and REQ-SEPHARMAMANUFACTURING-017 (negative pressure isolation). The 1 microgram per cubic metre breathing-zone limit is 10% of the OEL, providing a safety factor of 10 per ICH Q11 and ISPE Risk-MaPP guidance. Granulation-to-dryer and dryer-to-mill transfers are the highest exposure risk points in the OSD line because they involve open powder handling of wet and dry API-containing material. | subsystem, granulation-blending, session-549, sil-2, idempotency:sub-gb-containment-549
SUB-REQ-024 | While in sensor-degraded state, the PAT Subsystem SHALL suspend real-time CQA model evaluation on the affected sensor channel within 10 seconds of degradation detection, continue acquisition on all unaffected channels (minimum: 2 of 3 sensor channels must remain operational before a full-system safe-state transition is required), present manual sampling prompts to operators within 60 seconds of each 15-minute interval expiry with sample identification barcodes, and record all manual sample submissions with timestamps and operator ID for MES EBR integration within 30 seconds of submission. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Derived from SUB-REQ-006. The 10-second suspension window is the maximum acceptable delay before a degraded channel could contribute an erroneous CQA estimate to the diversion model. The 2-of-3 channel floor ensures the PAT subsystem retains meaningful CQA coverage during single-sensor failure without triggering a full production halt; loss of 2+ sensors removes the basis for continued real-time release. The 60-second prompt window is the maximum allowable latency before a manual sampling event is considered missed under the degraded-mode protocol. | pat-subsystem, degraded-mode, session-554, supersedes:SUB-REQ-006, idempotency:sub-pat-degraded-quantified-554
SUB-REQ-025 | The Rotary Tablet Press SHALL monitor upper punch compression force at each station on every rotation and reject tablets where compression force deviates from the target setpoint by more than ±5 kN, using a pneumatic ejector actuating within 200 ms of ejection point detection. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Compression force is the primary determinant of tablet hardness and dissolution profile. A ±5 kN tolerance corresponds to a ±15% hardness variation (validated per ICH Q8) beyond which dissolution rate changes by >10%, risking sub-therapeutic dosing. Per-station monitoring is required because tooling wear is station-specific — a worn punch on station 14 will not be caught by average-force monitoring. The 200 ms ejection window is derived from the turret geometry at maximum 120 RPM: 500 ms/revolution ÷ 72 stations = 6.9 ms per station; 200 ms allows for the physical distance from detection to diverter. | subsystem, tablet-compression, sil-2, session-556, idempotency:sub-tc-press-force-556
SUB-REQ-026 | The Tablet In-Process Control System SHALL sample every 30th tablet for individual weight, hardness, and thickness measurement, and shall update the press fill-depth servo setpoint within 3 measurement cycles when the running mean weight deviates by more than ±1.5% from the target. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | USP <905> content uniformity requires weight variation <5% RSD. Sampling every 30th tablet at 120 RPM gives one sample every 1.5 seconds, providing trend data fast enough to detect gradual fill-depth drift before it exceeds the 5% USP limit. The ±1.5% control band provides a correction margin 3× narrower than the limit — consistent with ICH Q8 process analytical technology guidance for real-time release. | session-556, idempotency:sub-tc-ipc-weight-556
SUB-REQ-027 | When a guard door on the Rotary Tablet Press is opened, the Tablet Compression Subsystem SHALL de-energise the main drive motor and engage the mechanical turret brake within 500 ms, and SHALL prevent re-energisation until the guard door is confirmed closed and a positive LOTO key removal is electronically verified by the MES LOTO Registry Module. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Hazard H-007 (mechanical entrapment in rotating turret) is rated severity:critical, SIL-2 per IEC 61508 (Functional safety of electrical/electronic/programmable electronic safety-related systems). The 500 ms stop time is derived from the turret inertia at 120 RPM — stopping within half a revolution ensures no punch station can complete a full stroke after the guard opens. MES LOTO verification creates an electronic record satisfying 21 CFR Part 11 and FDA GMP audit requirements for every maintenance access event. | session-556, idempotency:sub-tc-loto-guard-556
SUB-REQ-028 | The Tablet Compression Containment Housing SHALL maintain negative pressure of -15 Pa (±3 Pa) relative to the surrounding cleanroom at all times during press operation, and SHALL trigger an audible alarm and initiate an automatic press hold within 5 seconds when pressure differential exceeds -10 Pa (loss-of-containment threshold). | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Hazard H-001 (airborne potent compound exposure, OEL 1-10 µg/m³) is rated severity:critical, SIL-2. MoP basis: -15 Pa containment setpoint derived from EU GMP Annex 1 pressure differential specification (≥10 Pa between classified zones); the ±3 Pa tolerance is consistent with ISPE Baseline Guide Vol. 2 (Sterile Manufacturing Facilities) pressure measurement accuracy requirements for unidirectional flow zones. | reqs-eng-session-566
SUB-REQ-029 | The Tablet Compression Subsystem SHALL read the RFID tag on each punch and die station at press startup and shall prevent press operation if any station has accumulated more than 500,000 compressions or if any RFID tag read fails, logging the failed station to the MES batch record. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Punch tip fracture (failure mode from the H-007 scenario — the 90-minute downtime event) is directly correlated with cumulative compression cycles. The 500,000 compression limit is the manufacturer-validated service life for S7 tool steel at 80 kN maximum force. RFID tracking is required rather than a paper log because 21 CFR Part 11 requires electronic records for all GMP-critical maintenance activities; a failed read treated as an error is a fail-safe — a missing RFID cannot be assumed to be a new punch. | session-556, idempotency:sub-tc-tooling-rfid-556
SUB-REQ-030 | When one of the three Tablet In-Process Control System measurement channels (weight, hardness, or thickness) fails, the Tablet Compression Subsystem SHALL continue press operation at reduced throughput (maximum 60% of nominal RPM) with manual sampling at 5-minute intervals substituting for the failed channel, and SHALL record the degraded-mode start time and reason in the MES batch record. | subsystem-requirements | Subsystem Requirements |  | Demonstration | 86 |  | A single IPC channel failure (e.g., weight probe jam) does not invalidate product quality if manual sampling is substituted at sufficient frequency. At 60% RPM (maximum 72 RPM), production output is 3,000-4,000 tabs/min; manual sampling every 5 minutes gives a sample of approximately 15,000-20,000 tablets, consistent with the USP <905> sampling plan minimum. Forcing degraded mode to 60% RPM provides headroom for operators to manage the increased manual workload without falling behind. This is consistent with SYS-REQ-009 degraded production mode. | session-556, idempotency:sub-tc-ipc-degraded-556
SUB-REQ-031 | The PAT Subsystem CQA model evaluation and diversion actuation function SHALL be implemented on a hardware architecture achieving at least Hardware Fault Tolerance (HFT) of 1 (IEC 61508 SIL-3 compliant), with the DAC Workstation having a redundant hot-standby instance; the standby instance SHALL assume primary control within 5 seconds of primary failure without loss of the current diversion decision state. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | SIL-3 IEC 61508 (Functional safety of electrical/electronic/programmable electronic safety-related systems): architectural analysis alone (HFT=1 calculation) does not satisfy IEC 61508 SIL-3 requirements. The hardware fault tolerance must be demonstrated by hardware-in-the-loop testing — injecting primary channel failure and confirming the secondary channel takes over within the specified 500ms window. VER-REQ-047 specifies this failover test procedure. Analysis is insufficient as the sole verification method for a SIL-3 safety function. | session-561, validation, pat, sil-3, h-004, architecture, redundancy, idempotency:session561-sub-pat-sil3-hft1-architecture, idempotency:session561-sub-pat-sil3-hft1-architecture
SUB-REQ-036 | The Process Analytical Technology Subsystem SHALL operate from a dedicated 230V AC 50Hz UPS-backed power supply providing minimum 4 hours of autonomous operation on battery, with automatic power failure alarm to the MES within 10 seconds of mains loss. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | The PAT subsystem is Powered (UHT trait) and SIL-3 rated. A power failure during active CQA model evaluation must not result in silent loss of diversion control. The 4-hour battery backup ensures continued operation through a typical mains supply incident. The 10-second alarm limit ensures the operator has adequate warning to switch to manual sampling before the UPS is depleted. Addresses lintHigh finding 7. | session-562, validation, pat, power, sil-3, h-004, idempotency:session562-sub-pat-power-supply
SUB-REQ-037 | The PAT Subsystem SHALL provide a manual CQA override interface accessible to the QC Analyst role, enabling a qualified operator to override a CQA model limit violation and continue production with enhanced manual sampling, with the override action and justification text recorded in the EBR within 60 seconds of override activation. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | The PAT Subsystem is classified as Functionally Autonomous (UHT trait) and must have a human-in-the-loop override per IEC 61508 SIL-3 requirement for safety-related autonomous systems. This requirement addresses lintHigh finding 16. The QC Analyst role restriction prevents unauthorised overrides. EBR logging within 60 seconds ensures audit trail completeness under 21 CFR Part 11. | session-562, validation, pat, override, sil-3, h-004, autonomy, idempotency:session562-sub-pat-manual-override
SUB-REQ-038 | The Manufacturing Execution System SHALL implement a watchdog timer that monitors core EBR processing heartbeat at 30-second intervals, and when three consecutive heartbeats are missed, SHALL log a system health alert to the CMMS, switch the SCADA operator display to a system-unavailable state, and prevent new batch record initiation until the MES health check passes. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | The MES is classified as Functionally Autonomous (UHT trait) and must have a watchdog and fail-safe state per IEC 62443-4-2 (Security for industrial automation and control systems). This requirement addresses lintHigh finding 17. The 30-second heartbeat interval and 3-miss threshold (90 seconds total) provides a balance between false-alarm avoidance and timely failure detection. The fail-safe state prevents new batch records from being initiated on a potentially compromised system. | session-562, validation, mes, watchdog, sil-2, h-006, autonomy, idempotency:session562-sub-mes-watchdog
SUB-REQ-039 | The Tablet Compression Subsystem SHALL operate from a dedicated 400V AC 50Hz 3-phase power supply with a soft-starter providing controlled ramp-up to prevent current surge, and SHALL have a monitored emergency power-off (EPO) circuit that de-energises the main drive within 200ms of activation, with EPO status monitored by the MES LOTO registry. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | The Rotary Tablet Press and associated IPC system are Powered (UHT trait) physical components requiring defined power supply parameters for safe operation. The 200ms EPO response directly supports the H-007 safe state (equipment de-energised and mechanically braked) and integrates with the LOTO registry requirement (SUB-REQ-011). Addresses lintHigh finding 8 and 13. | session-562, validation, tablet-compression, power, sil-2, h-007, idempotency:session562-sub-tc-power-epo
SUB-REQ-040 | The Granulation and Blending Subsystem SHALL operate from 400V AC 50Hz 3-phase power supply for the High Shear Granulator impeller (rated 37kW) and Fluid Bed Dryer heating element (rated 30kW), with power monitoring that triggers an MES alarm if supply voltage deviates more than 10 percent from nominal, and an EPO that de-energises both machines within 500ms of activation. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | The High Shear Granulator and Fluid Bed Dryer are Powered (UHT trait) physical components. Power deviations exceeding 10 percent affect impeller speed control and heating performance, directly impacting granule LOD CQA. The 500ms EPO supports H-001 and H-003 safe state transitions. Addresses lintHigh findings 9, 12, and 15. | session-562, validation, granulation-blending, power, sil-2, h-001, idempotency:session562-sub-gb-power-supply
SUB-REQ-041 | The Film Coating Subsystem SHALL operate from 400V AC 50Hz 3-phase power supply for the pan coater drive (rated 22kW) and inlet air heating system (rated 45kW), with power consumption monitoring that logs actual energy consumption per batch cycle to the MES for OEE calculation, and an EPO that de-energises all drives within 500ms. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | The Film Coating Subsystem is a Powered (UHT trait) physical component requiring defined electrical supply parameters. The power consumption logging supports the OEE and process monitoring requirements of SYS-REQ-017. The 500ms EPO response supports safe-state transition for hazards involving coating materials. Addresses lintHigh finding 11. | session-562, validation, film-coating, power, idempotency:session562-sub-fc-power-supply
SUB-REQ-042 | The Containment and Environmental Control Subsystem SHALL operate from a UPS-backed 230V AC power supply providing minimum 2 hours of autonomous operation on battery for all monitoring and alarm functions, and SHALL maintain HVAC damper positions during power interruption (fail-secure to exhaust mode) to preserve containment integrity. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | The Containment Subsystem must remain operational during power failures to maintain H-001 safe state (HVAC switched to full exhaust). The fail-secure exhaust mode on power loss is a SIL-2 safety function. The 2-hour battery runtime covers the maximum expected time for emergency generator activation and transfer. Addresses lintHigh finding indirectly through physical safety system power requirements. | session-562, validation, containment, power, sil-2, h-001, idempotency:session562-sub-cec-power-ups
SUB-REQ-043 | The Manufacturing Execution System server hardware SHALL be housed in a dedicated server rack with dual redundant power supplies (each rated for 100 percent load), located in an access-controlled equipment room separate from the production floor, with physical access logged to the CMMS. | subsystem-requirements | Subsystem Requirements |  | Inspection | 86 |  | The MES is a software subsystem but requires physical server hardware (Physical Object embodiment). Dual redundant PSUs directly support MES availability for SIL-2 EBR continuity. Physical access control to the server room is a 21 CFR Part 11 data integrity requirement. Inspection is the appropriate verification method for physical installation and access control measures. Addresses lintHigh finding 1. | session-562, validation, mes, hardware, physical, 21cfr11, idempotency:session562-sub-mes-server-hardware
SUB-REQ-044 | The system SHALL not permit entry to Normal Production mode unless all of the following conditions are met: all equipment IQ/OQ/PQ qualification records are current and QA-approved; all PAT instruments have passed system suitability checks against certified reference materials; all process parameters in the batch record have been reviewed and approved by Production Supervisor; and no active deviation from the previous campaign remains open. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Startup mode entry criteria are safety-critical controls for product quality and batch release. Undefined or unenforced entry criteria allow production to start on non-qualified equipment, risking OOS product release (H-004). This requirement formalises the Startup/Qualification mode exit condition into a verifiable pre-production gate. Test verification requires a functional check of each pre-production gate in the MES workflow. | session-562, validation, mode-coverage, startup, mes, idempotency:session562-sub-startup-entry-criteria
SUB-REQ-045 | When the system transitions from Emergency Stop mode, the Manufacturing Execution System SHALL require explicit QA Manager electronic signature in the EBR, enforce a mandatory 30-minute environmental clearance period with air monitoring below 50% OEL, and generate a deviation record linked to the triggering alarm event, before permitting any production equipment re-energisation. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Emergency Stop mode exit is a safety-critical transition. Premature re-energisation after a containment breach (H-001) or mechanical jam (H-007) is the primary cause of secondary incidents in pharmaceutical manufacturing. The QA Manager sign-off requirement is mandated by 21 CFR Part 211 supervisory review requirements. The 30-minute clearance period is the minimum time to confirm environmental decontamination by continuous air monitoring. | reqs-eng-session-566
SUB-REQ-046 | While in Maintenance mode, the system SHALL prevent equipment power-on by any means (HMI, PLC, remote command) for any equipment with an active LOTO lock applied, and SHALL display the LOTO status (locked, applied-by, time-applied) on the MES operator display for all maintenance-targeted equipment. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Maintenance mode requires hardware and software barriers to prevent accidental equipment energisation while personnel are in contact with moving parts (H-007). The LOTO status display requirement supports the operator's situational awareness during multi-person maintenance activities and is a OSHA 29 CFR 1910.147 (Control of Hazardous Energy) compliance requirement. Test verification requires attempting equipment energisation via all three command paths while LOTO is active. | session-562, validation, mode-coverage, maintenance, loto, sil-2, h-007, idempotency:session562-sub-maintenance-loto-display
SUB-REQ-047 | While in Degraded Production mode, the system SHALL quarantine all completed batches in MES quarantine status within 60 seconds of batch completion, prevent real-time release of any quarantined batch, and require a QA Manager electronic signature in the EBR before advancing a batch from quarantine following traditional offline QC release (HPLC content uniformity: n≥6, RSD≤2.0%, mean within ±5.0% of label claim). | subsystem-requirements | Subsystem Requirements |  | Test | 71 |  | Derived from STK-REQ-009 (maintain product quality assurance during PAT sensor degradation) and SYS-REQ-009 (degraded mode production at reduced throughput with traditional QC release). Automatic quarantine within 60 seconds prevents inadvertent real-time release of batches produced without full PAT monitoring. HPLC acceptance criteria (n≥6, RSD≤2.0%) are the validated offline method for content uniformity per USP <905> when real-time PAT release is suspended. | session-562, validation, mode-coverage, degraded, sil-3, h-004, rtrt, idempotency:session562-sub-degraded-rtr-block
SUB-REQ-048 | The Containment and Environmental Control Subsystem SHALL detect airborne API concentration above the OEL action limit (80 percent of OEL) and SHALL automatically: (a) activate the Emergency Stop function; (b) close all material transfer valve actuators at the affected station within 5 seconds; (c) switch room HVAC to 100 percent exhaust through HEPA filtration within 15 seconds; and (d) trigger an evacuation alarm audible at 85 dB at 1 metre from the nearest alarm sounder. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | H-001 hazard requires automated response to containment breach without relying on operator action. The 5-second valve closure and 15-second HVAC response times are derived from the airborne dispersion modelling showing that a 20-second response prevents operator dose from exceeding the STEL (Short-Term Exposure Limit). The 85 dB alarm standard meets EN ISO 7731 workplace emergency alarm requirements. | session-562, validation, containment, sil-2, h-001, emergency, idempotency:session562-sub-cec-breach-autoresponse
SUB-REQ-049 | The Containment and Environmental Control Subsystem SHALL perform continuous air monitoring at each sampling point at a minimum frequency of 1 sample per 60 seconds during Normal Production and Degraded Production modes, and SHALL maintain air monitoring data in the EBR for a minimum of 10 years for regulatory inspection, with data export in CSV and PDF formats. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Continuous air monitoring at 1-sample/60-second frequency is required to detect rapid concentration changes before operator exposure reaches the STEL, which is typically measured over 15 minutes. The 10-year data retention requirement derives from 21 CFR Part 211.68 record retention requirements for pharmaceutical manufacturing. Test verification confirms both the monitoring frequency and the data retention/export functionality. | session-562, validation, containment, monitoring, sil-2, h-001, idempotency:session562-sub-cec-air-monitoring-freq
SUB-REQ-050 | When the Cleaning Validation results for any swab location exceed the acceptance limit, the Manufacturing Execution System SHALL automatically quarantine the next batch associated with that equipment, alert the QA Manager via SCADA notification and email, and prevent batch record release until the QA Manager reviews the cleaning deviation and signs the EBR for the affected equipment. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Cleaning validation failure is the primary trigger for H-002 cross-contamination risk. Automatic quarantine prevents accidental release of potentially contaminated product while the cleaning deviation is investigated. This requirement operationalises the Changeover/Cleaning scenario from the ConOps where a first cleaning attempt fails at location 7. The email and SCADA dual notification ensures the QA Manager is alerted even if not actively monitoring the SCADA screen. | session-562, validation, mes, changeover, sil-3, h-002, idempotency:session562-sub-mes-cleaning-fail-quarantine
SUB-REQ-051 | The Material Handling and Dispensing Subsystem SHALL enforce a two-person independent check for all API dispensing operations above 1kg, with electronic confirmation from both operators required in the MES before the dispensing step is closed in the EBR, preventing advancement to the next batch step until both confirmations are received. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Two-person API dispensing check is a 21 CFR Part 211 critical step verification requirement for potent compounds. The EBR workflow gate preventing step advancement until both confirmations are received ensures the check is performed and documented before product enters the manufacturing process. Incorrect API quantity dispensed (H-002) is a catastrophic quality failure mode. | session-562, validation, material-handling, sil-3, h-002, api-dispensing, idempotency:session562-sub-mhd-two-person-api
SUB-REQ-052 | The Tablet Compression Subsystem SHALL perform a real-time metal detection check on the tablet stream at the press output, and when a metallic contaminant is detected, SHALL automatically activate the tablet rejection mechanism to divert a minimum of 10 tablets before and after the detection point to the reject stream, and SHALL generate a critical alarm in the MES with the detected fragment size estimate if available. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Metal detection at the press output is the last automated line of defence against metallic contamination from broken punch tooling (Tablet Press Jam scenario). The 10-tablet pre/post-detection rejection window accounts for the detection zone uncertainty and tablet discharge timing. A single metallic fragment in a batch poses a patient safety risk categorised as a critical defect per FDA 21 CFR Part 211.84. | session-562, validation, tablet-compression, metal-detection, sil-2, idempotency:session562-sub-tc-metal-detection
SUB-REQ-053 | The Granulation and Blending Subsystem SHALL monitor for dust explosion risk by measuring dust concentration at the FBD exhaust duct using a continuous dust sensor, and when concentration exceeds 25 percent of the Lower Explosion Limit (LEL), SHALL activate nitrogen inerting flow, reduce FBD airflow to minimum circulation rate, and generate a SIL-2 alarm to the MES within 10 seconds. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Pharmaceutical powder dust explosion (H-003) is a catastrophic hazard at LEL concentrations. The 25 percent LEL threshold provides a two-fold safety margin below the minimum 50 percent LEL action concentration per ATEX (Directive 2014/34/EU) hazardous area classification. Nitrogen inerting prevents the dust-air mixture from reaching the minimum oxygen concentration required for ignition. The 10-second response time is derived from the maximum dust cloud dispersion rate in the FBD chamber. | session-562, validation, granulation-blending, dust-explosion, sil-2, h-003, atex, idempotency:session562-sub-gb-dust-explosion-inerting
SUB-REQ-054 | The Packaging and Serialisation Subsystem SHALL perform 100 percent vision inspection of each blister cavity for correct tablet count, absent tablets, broken tablets, and foreign particles, and SHALL reject any blister pack where the vision system confidence score for any cavity falls below 95 percent, logging rejected pack IDs and rejection reasons to the MES EBR. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Vision inspection of packaging is the final automated quality gate before product release. Absent or broken tablets in a blister pack constitute a critical defect under 21 CFR Part 211.84 that would require batch recall if released to market. The 95 percent confidence threshold is a conservative limit reflecting the validated detection sensitivity for the smallest tablet size variant in the product range. | session-562, validation, packaging, vision-inspection, sil-2, idempotency:session562-sub-pkg-vision-inspection
SUB-REQ-055 | The Laboratory Information Management System (LIMS) interface SHALL receive all QC sample requests from the MES within 30 seconds of sample registration in the EBR, return analytical results to the MES within 5 minutes of result entry in LIMS for samples flagged as time-critical (real-time release), and retain rejected results with the rejection reason in both LIMS and MES audit trails. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | LIMS-MES integration latency directly affects real-time release decision cycle time. The 30-second request receipt and 5-minute result return limits are derived from the maximum allowable hold time for in-process samples awaiting analytical results before product quality degrades. The dual audit trail requirement supports 21 CFR Part 11 data integrity across both systems. | session-562, validation, lims, mes, real-time-release, idempotency:session562-sub-lims-mes-latency
SUB-REQ-056 | The Electronic Batch Record Engine within the Manufacturing Execution System SHALL generate a batch review summary report in PDF/A format within 15 minutes of batch completion, including all critical process parameter trends, in-process control results, deviation summary, and a compliance checklist against the approved product specification, available for QA Manager review without additional data queries. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Batch review report generation within 15 minutes of batch completion is required for same-shift QA review in a 12-hour production schedule. PDF/A format is required for long-term archival per ISO 19005 as mandated by EU GMP Annex 11 electronic record retention requirements. Test verification confirms the report is generated automatically, the 15-minute SLA is met, and the report content matches the EBR data. | session-562, validation, mes, ebr, batch-review, 21cfr11, idempotency:session562-sub-mes-batch-report-gen
SUB-REQ-057 | The Process Analytical Technology Subsystem SHALL maintain a rolling 30-day archive of all CQA model inputs, model outputs, diversion decisions, and calibration check results in a tamper-evident audit log, accessible to QA Analyst and QA Manager roles, exportable in CSV format for retrospective trend analysis and regulatory inspection. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | A 30-day retrospective PAT audit log is required to support deviation investigations, regulatory inspections, and real-time release retrospective reviews under 21 CFR Part 211.180 and EU GMP Annex 11. The tamper-evident requirement is mandated by 21 CFR Part 11 audit trail provisions. Test verification confirms the log is populated correctly, exports are accurate, and tamper evidence is detectable. | session-562, validation, pat, audit-log, sil-3, h-004, idempotency:session562-sub-pat-audit-log
SUB-REQ-058 | The Process Analytical Technology Subsystem SHALL provide a qualified user override mechanism that enables a QC Analyst or Production Supervisor to suspend automated CQA-based batch diversion, subject to mandatory EBR electronic signature for each override event, a maximum override duration of 60 minutes without re-authorisation, and automatic restoration of autonomous CQA evaluation when the override expires. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | IEC 61508 (Functional safety of E/E/PE safety-related systems) Part 3 requires that functionally autonomous safety systems provide a defined and auditable override mechanism. The PAT subsystem makes autonomous SIL-3 diversion decisions; the override must be bounded in duration and logged to prevent unconstrained bypass of the H-004 safety function while allowing legitimate quality judgement by trained personnel. | session-564, validation, pat, sil-3, h-004, functional-autonomy, override, idempotency:session564-sub-pat-autonomy-override
SUB-REQ-059 | The Granulation and Blending Subsystem SHALL be installed within a dedicated ISO 8 (Grade D) cleanroom bay, with all product-contact surfaces constructed from 316L stainless steel, and the equipment train (high-shear granulator, fluid bed dryer, bin blender) enclosed in a shared contained material transfer system using ANSI/ISPE OEB 4-compatible transfer connections. | subsystem-requirements | Subsystem Requirements |  | Inspection | 86 |  | Physical installation constraints for the granulation and blending subsystem are set by GMP cleanroom classification requirements and potent compound containment requirements (H-001, OEB 4). The 316L stainless steel and OEB 4 transfer connections are mandated by cGMP and product safety requirements. This requirement defines the physical embodiment of the subsystem to resolve the ontological mismatch with its Substrate classification. | session-565, granulation-blending, physical-embodiment, lint-fix-lh2, idempotency:ses565-blend-physical-embodiment, idempotency:ses565-blend-physical-embodiment
SUB-REQ-060 | The Process Control System (PCS) SHALL operate from a 24 VDC power supply with a maximum consumption of 500 W per PLC chassis, supported by an uninterruptible power supply (UPS) providing a minimum 30-minute backup at full load, and SHALL annunciate a power failure alarm within 2 seconds of utility power loss. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | PCS power supply and UPS backup requirements are needed to ensure continued operation of safety interlocks and LOTO enforcement logic during utility power failures. The 30-minute UPS duration is derived from the minimum time required to complete a controlled batch shutdown and reach safe state. Without a defined power budget, the PCS cabinet and UPS cannot be correctly specified during detailed design. | session-565, process-control, power-supply, ups, lint-fix-lh6, idempotency:ses565-pcs-power-budget, idempotency:ses565-pcs-power-budget
SUB-REQ-061 | The Manufacturing Execution System SHALL implement a hardware watchdog timer with a 30-second timeout that triggers a controlled safe-state transition (suspend batch execution, issue HVAC failsafe command, alert operators) if MES software fails to send a heartbeat signal; and SHALL provide a qualified user emergency override capability enabling a Production Supervisor to halt all MES-controlled automated functions within 10 seconds via a dedicated physical E-STOP button at each operator workstation. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | The MES executes batch recipes autonomously and controls safety-critical equipment interlocks (LOTO, containment). IEC 61508 (Functional safety of E/E/PE safety-related systems) requires that Functionally Autonomous systems at SIL-2 have hardware watchdog supervision and a human-accessible override. The 30-second watchdog timeout is the minimum interval that permits software restart without a spurious safe-state alarm during normal MES operation. | session-565, mes, watchdog, override, functionally-autonomous, sil-2, lint-fix-lh7, idempotency:ses565-mes-watchdog-override, idempotency:ses565-mes-watchdog-override
SUB-REQ-062 | The Containment and Environmental Control Subsystem SHALL install differential pressure transmitters at each controlled cleanroom boundary (weigh booth to corridor, granulation bay to corridor, and coating/packaging bay to corridor), temperature probes and humidity sensors at product exposure height (0.8–1.2 m above floor) in each classified bay, with all sensor housings constructed from 316L stainless steel and certified to ISO 8 cleanroom installation standards per EU GMP Annex 1. | subsystem-requirements | Subsystem Requirements |  | Inspection | 86 |  | SYS-REQ-025 specifies the physical sensor placement and material standards required for cleanroom environmental monitoring — the SYS requirement is facility-level and needs decomposition to the Containment and Environmental Control Subsystem. The installation positions are defined by EU GMP Annex 1 and ICH Q10 (Pharmaceutical Quality System) requirements for representative environmental monitoring. 316L stainless steel prevents corrosion and microbial harbourage in classified areas. | session-565, validation, environmental-control, sensor-installation, sil-1, idempotency:session565-sub-envctl-sensor-installation
SUB-REQ-063 | The HVAC Air Handling Unit SHALL maintain cleanroom supply air conditions within the range 20±2°C (temperature), 45±5% RH (humidity), and a minimum of 20 air changes per hour for ISO 7 cleanroom grades, as specified in EU GMP Annex 1 (Manufacture of Sterile Medicinal Products). | subsystem-requirements | Subsystem Requirements |  | Test |  |  | EU GMP Annex 1 and SYS-REQ-022 mandate ISO 7/8 cleanroom classification with specific temperature, humidity, and ACH thresholds. Deviation from these conditions compromises cleanroom classification, product quality (hygroscopic API degradation above 50% RH), and GMP compliance, triggering a batch rejection event under the EBR. | subsystem, containment, hvac, environmental-control, sil-2, session-548, idempotency:sub-cec-hvac-cleanroom-conditions-548
SUB-REQ-064 | The HVAC Air Handling Unit SHALL maintain a minimum differential pressure of +10 Pa between adjacent cleanroom grades and -12.5 Pa inside the Potent Compound Isolator relative to the surrounding cleanroom, with the Differential Pressure Monitoring Controller achieving setpoint within 30 seconds of any disturbance. | subsystem-requirements | Subsystem Requirements |  | Test |  |  | SYS-REQ-004 specifies -12.5 Pa minimum inward pressure in OEB 4/5 containment zones. The +10 Pa cascade for adjacent ISO grades prevents cross-contamination between production areas. 30-second setpoint recovery is derived from the time a cleanroom door can remain open during normal operation without compromising room classification (EU GMP Annex 1 Section 4.4). | subsystem, containment, hvac, pressure-cascade, sil-2, session-548, idempotency:sub-cec-hvac-pressure-cascade-548
SUB-REQ-065 | When the Containment Safety PLC detects a containment integrity failure (isolator pressure above -5 Pa for more than 5 seconds, or airborne API concentration above 80% OEL), the Containment and Environmental Control Subsystem SHALL transition to the safe state — switching HVAC to 100% exhaust mode, sealing supply air dampers, and triggering a Level 1 alarm — within 30 seconds of detection. | subsystem-requirements | Subsystem Requirements |  | Test |  |  | SIL-2 safe state requirement per IEC 61508 (Functional safety of E/E/PE safety-related systems). The H-001 hazard (airborne potent compound exposure) safe state is defined as maximum exhaust to dilute any released API below OEL. 30-second transition time is the maximum allowable period for hazardous concentration build-up before exceeding IDLH limits for OEB 4/5 compounds, based on worst-case room volume and release rate modelling. | subsystem, containment, safe-state, sil-2, h-001, emergency, session-548, idempotency:sub-cec-safe-state-breach-548
SUB-REQ-066 | The Environmental Monitoring System SHALL generate an audible and visual alarm within 60 seconds of any cleanroom environmental parameter (temperature, RH, or differential pressure) exceeding its alarm limit, and SHALL transmit the alarm event to the MES EBR engine via OPC UA within the same 60-second window. | subsystem-requirements | Subsystem Requirements |  | Test |  |  | SYS-REQ-006 specifies 60-second alarm response for environmental excursions. The simultaneous MES notification ensures that the deviation is embedded in the electronic batch record at the time of occurrence, satisfying 21 CFR Part 11 (Electronic records and electronic signatures) audit trail requirements and enabling automatic batch deviation records per SYS-REQ-019. | subsystem, containment, ems, monitoring, alarm, session-548, idempotency:sub-cec-ems-alarm-response-548
SUB-REQ-068 | The Containment and Environmental Control Subsystem SHALL maintain cleanroom particle counts at or below ISO 14644-1 Class 7 limits (352,000 particles per cubic metre at 0.5 µm) in granulation and compression bays during active production, verified by the airborne particle counter network at no less than 1 sample per 30 minutes. | subsystem-requirements | Subsystem Requirements |  | Test |  |  | SYS-REQ-022 requires ISO 7 cleanroom classification in granulation and compression bays. Continuous particle monitoring at 30-minute intervals meets ISO 14644-1 (Cleanrooms and associated controlled environments) statistical sampling requirements and detects filter failure or human incursion events before product contamination occurs. | subsystem, containment, monitoring, cleanroom, session-548, idempotency:sub-cec-particle-count-iso7-548
SYS-REQ-001 | The system SHALL operate the production sequence — from raw material dispense through granulation, blending, compression, and packaging — at a nominal throughput of 300,000 tablets per shift (12-hour shift), with OEE tracked continuously by the MES and reported hourly. | system-requirements | System Requirements | ubiquitous | Test | 86 |  | Derived from STK-001 (OEE ≥ 75%). 300,000 tablets/12-hour shift is the system design capacity from the Normal Production Campaign scenario; OEE tracking is the mechanism by which compliance with the 75% OEE threshold is measured and demonstrated. | idempotency:sys-pharma-throughput-001
SYS-REQ-002 | The system SHALL generate, execute, and archive electronic batch records (EBRs) with electronic signatures, access controls, audit trails, and backup intervals not exceeding 15 minutes, with record integrity verified by cryptographic hash on every write operation. | system-requirements | System Requirements | ubiquitous | Test | 86 |  | Derived from STK-002 (21 CFR Part 11 / EU Annex 11 EBR compliance). Cryptographic hashing on every write and 15-minute backup intervals are the technical controls that satisfy data integrity requirements. 15-minute interval ensures a maximum of 15 minutes of data loss in a catastrophic failure, meeting typical GMP data recovery expectations. | session-564, validation, ver-method-upgraded, ebr, 21cfr11, sil-2, h-006
SYS-REQ-003 | The system SHALL acquire PAT sensor data (NIR, Raman, laser diffraction) at a minimum sample interval of 30 seconds, evaluate CQA models within 5 seconds of acquisition, and actuate automatic batch diversion valves within 2 seconds of a CQA limit exceedance. | system-requirements | System Requirements | ubiquitous | Test | 86 |  | Derived from STK-003 (real-time PAT with automatic diversion). 30-second sampling ensures sufficient time resolution for blend uniformity and granule size monitoring. 5-second model evaluation and 2-second actuation give a total response latency of 7 seconds, which is within the 10-second diversion window before the affected material exits the process vessel. | idempotency:sys-pharma-pat-003
SYS-REQ-004 | The system SHALL maintain negative pressure isolation in potent compound processing enclosures (OEB 4/5 compounds, OEL < 1 µg/m³) with a minimum inward airflow velocity of 0.5 m/s at all open access points, continuous real-time airborne particle monitoring at operator breathing zone, and automatic enclosure lockdown when particle concentration exceeds 20% of OEL alarm threshold. | system-requirements | System Requirements | ubiquitous | Test | 86 |  | Derived from STK-REQ-004 (OEL containment integrity) and H-001 airborne potent compound exposure hazard. MoP basis: 0.5 m/s inward airflow specification derived from EU GMP Annex 1 (2022) Section 4.6 (negative pressure room design for hazardous substances) and COSHH (Control of Substances Hazardous to Health) Regulation 7 engineering control hierarchy; -50 Pa minimum pressure differential consistent with ISPE Risk-MaPP (Baseline Guide for Risk-Based Manufacture of Pharmaceutical Products) OEB 4 containment strategy. | reqs-eng-session-566, h-001
SYS-REQ-005 | When an emergency stop is triggered (by operator actuator, interlock, or automatic safety function), the system SHALL de-energise all drive systems within 3 seconds, close all product-transfer valves within 5 seconds, and achieve full equipment standstill within 10 seconds. | system-requirements | System Requirements | event | Test | 86 |  | Derived from STK-005 (emergency stop ≤ 10 seconds) and EN ISO 13850. 3-second drive de-energisation and 5-second valve closure are the subsystem-level allocations of the 10-second total emergency stop time budget. These values are achievable with standard pneumatic valve actuators and safety-rated drive modules. | idempotency:sys-pharma-estop-005
SYS-REQ-006 | While in Normal Production mode, the system SHALL continuously monitor cleanroom differential pressure, temperature (20±2°C), and relative humidity (45±5% RH), generating an alarm within 60 seconds of any parameter exceeding its alert limit, and a production halt within 120 seconds of any parameter exceeding its action limit. | system-requirements | System Requirements | state | Test | 86 |  | Derived from STK-011 (ISO Class 7 cleanroom maintenance) and Cleanroom environmental control failure hazard. 60-second alert and 120-second action response times align with EU GMP Annex 1 environmental monitoring expectations. Temperature and humidity affect granule moisture content and tablet hardness; action limits require production halt to protect batch quality. | lint-ack-ontological-mismatch, session-565, lint-ack-normal-production-mode-not-physical, session-567, h-005
SYS-REQ-007 | The system SHALL record and maintain a full batch genealogy database linking every finished product unit to its input raw material lot numbers, equipment IDs, process parameter logs, and operator IDs, enabling recall scope determination for any batch within 4 hours. | system-requirements | System Requirements | ubiquitous | Test | 86 |  | Derived from STK-010 (material traceability). The genealogy database is the technical implementation of bidirectional traceability; it must be queryable to reconstruct batch history within FDA CDER 4-hour recall assessment window. All equipment IDs, operator IDs, and material lot numbers must be captured in real-time during processing. | idempotency:sys-pharma-genealogy-007
SYS-REQ-008 | The system SHALL guide operators through validated cleaning procedures during product changeover, verify cleaning completion via rinse water TOC analysis (≤ 500 µg/L TOC) and swab sampling, and prevent restart of the next production campaign until all cleaning verification steps are electronically signed and recorded in the EBR. | system-requirements | System Requirements | ubiquitous | Test | 86 |  | Derived from STK-007 (cross-contamination limits) and Product Changeover Cleaning Validation scenario. TOC ≤ 500 µg/L is the ICH Q3C Class 2 solvent threshold used as a surrogate for cleaning verification; electronic sign-off lock prevents operator bypass. The EBR lock is the enforcement mechanism ensuring cleaning validation is never skipped. | idempotency:sys-pharma-changeover-008
SYS-REQ-009 | When the PAT subsystem enters sensor-degraded mode, the system SHALL automatically switch to manual in-process testing mode with sampling every 15 minutes, maintain production at ≥ 50% nominal throughput, and alert the Production Supervisor with a prominent EBR annotation, within 30 seconds of sensor degradation detection. | system-requirements | System Requirements | event | Test | 86 |  | Derived from STK-009 (degraded production at ≥ 50% throughput) and PAT Sensor Drift Degraded Operation scenario. 15-minute manual sampling interval is the maximum interval consistent with EU GMP in-process testing requirements in the absence of continuous PAT monitoring. 30-second notification ensures operator awareness before manual testing regime begins. | idempotency:sys-pharma-degraded-009
SYS-REQ-010 | The system SHALL apply 2D DataMatrix barcodes encoding a unique serial number, GTIN, lot number, and expiry date to 100% of saleable units at the packaging line, with a barcode verification reject rate of less than 0.5% and aggregation data uploaded to the external serialization system within 2 hours of packaging lot completion. | system-requirements | System Requirements | ubiquitous | Test | 86 |  | Derived from STK-008 (EU FMD / US DSCSA serialization). GS1 DataMatrix is the mandated barcode standard under EU FMD Delegated Regulation 2016/161. 0.5% reject rate is the equipment supplier performance specification; 2-hour upload window satisfies the 24-hour regulatory reporting window with margin for data review. | idempotency:sys-pharma-serialization-010
SYS-REQ-011 | The system SHALL enforce electronic lockout verification for maintenance activities, preventing equipment restart while any active lockout device is registered, and logging all LOTO events with operator ID, timestamp, and equipment ID in the EBR. | system-requirements | System Requirements | ubiquitous | Test | 100 |  | Derived from STK-012 (LOTO PLd) and Tablet press mechanical entrapment hazard. Electronic lockout verification adds a software layer to physical LOTO that prevents inadvertent restart by a second operator; EBR logging creates the GMP evidence trail required for OSHA compliance and incident investigation. | idempotency:sys-pharma-loto-011
SYS-REQ-012 | The system SHALL enforce an automated in-process rejection of any tablet with weight outside ±5% of target, hardness outside specification range, or thickness outside ±2% of target, and shall reject the entire production segment when content uniformity AV exceeds 15.0 on L1 sampling. | system-requirements | System Requirements | ubiquitous | Test | 86 |  | Derived from STK-013 (pharmacopoeial specification compliance). Weight ±5%, hardness, and thickness ±2% are in-process control (IPC) limits defined in the product master batch record; automated rejection eliminates human judgment errors in OOS handling. AV > 15.0 triggers mandatory L2 retest or batch rejection per USP 905. | idempotency:sys-pharma-product-quality-012
SYS-REQ-013 | The system SHALL maintain worker occupational exposure below the compound-specific Occupational Exposure Limit (OEL) by enforcing the OEB containment strategy defined in the compound safety data sheet, and generating an alarm when airborne monitoring exceeds 80% of the OEL action limit. | system-requirements | System Requirements |  | Test | 86 |  | Worker protection from potent compound exposure is a primary stakeholder requirement (H-001, H-003). OEL compliance is mandated by COSHH (Control of Substances Hazardous to Health Regulations 2002) and OSHA 29 CFR 1910.1000 PEL requirements. The 80 percent alarm threshold provides a response window before the OEL action limit is breached. | reqs-eng-session-566, h-001
SYS-REQ-014 | The system SHALL support process validation per ICH Q8 (Pharmaceutical Development) and ICH Q11 (Development and Manufacture of Drug Substances) by recording all critical process parameters (CPPs), critical quality attributes (CQAs), and key process indicators (KPIs) for every batch in a retrievable electronic format suitable for prospective and concurrent validation programmes. | system-requirements | System Requirements |  | Analysis | 86 |  | ICH Q8 requires that CPPs and CQAs be identified, monitored, and documented as part of the validated design space. This system-level requirement ensures the manufacturing line generates the data required for regulatory filings (NDA, MAA). Analysis verification is appropriate because compliance with data completeness and format requirements can be demonstrated by reviewing the EBR data structure against ICH Q8 guidance. | session-562, validation, process-validation, ich-q8, idempotency:session562-sys-process-validation-014
SYS-REQ-015 | The system SHALL comply with EU Delegated Regulation 2016/161 (Falsified Medicines Directive) requirements for unique identifier placement, tamper-evident device application, and verification and decommissioning of unique identifiers at point of supply, and SHALL integrate with national medicines verification systems via the EMVO EMVS API. | system-requirements | System Requirements |  | Test | 86 |  | EU Delegated Regulation 2016/161 is a legal requirement for all prescription medicines placed on the EU market from 9 February 2019. Non-compliance results in inability to sell product in EU. Test verification requires a connection to the EMVS test repository to confirm that serialisation data is correctly formatted and accepted by the external system. | session-562, validation, serialisation, eu-fmd, regulatory, idempotency:session562-sys-eu-delegated-regulation-015
SYS-REQ-016 | The system SHALL implement machine safety controls compliant with EN ISO 13849-1 (Safety of machinery — Safety-related parts of control systems) for all rotating and moving equipment, achieving a minimum Performance Level d (PLd) for guard interlocks, emergency stops, and LOTO verification functions, with proof test intervals documented in the safety case. | system-requirements | System Requirements |  | Test | 86 |  | SIL-2 IEC 61508 requirements mandate that safety functions — not just their design documents — be verified by test. EN ISO 13849-1 (Safety of machinery: safety-related parts of control systems) compliance analysis (PLr, MTTFd, DC calculations) establishes the design meets the required performance level, but the safety functions themselves (E-stop response, guard interlock, brake engagement) must be tested under realistic operating conditions to demonstrate the actual realised performance level. Verification by Analysis alone is insufficient for SIL-2 functional safety claims. | session-562, validation, machine-safety, en-iso-13849, sil-2, idempotency:session562-sys-en-iso-13849-016, h-007
SYS-REQ-017 | The system SHALL calculate and display Overall Equipment Effectiveness (OEE) per the SEMI E10 equipment productivity standard, updated at least every 4 hours, decomposed into Availability, Performance, and Quality components, and SHALL generate an alert when OEE for any subsystem falls below 75 percent for more than one production shift. | system-requirements | System Requirements |  | Test | 86 |  | OEE tracking is a primary stakeholder requirement for production efficiency. The SEMI E10 standard provides an unambiguous OEE calculation methodology. The 75 percent threshold is the industry benchmark for world-class pharmaceutical manufacturing. Test verification is required because OEE calculation accuracy depends on the integration of downtime, speed loss, and quality rejection data streams from multiple subsystems. | session-562, validation, oee, production-efficiency, idempotency:session562-sys-oee-tracking-017
SYS-REQ-018 | The system SHALL enforce PAT qualification procedures per FDA Process Analytical Technology Guidance (2004) and ICH Q8, requiring calibration verification of all PAT instruments against certified reference materials before each campaign, with calibration status logged in the EBR and any out-of-calibration instrument triggering automatic suspension of real-time release. | system-requirements | System Requirements |  | Test | 86 |  | FDA PAT Guidance requires that PAT instruments be calibrated and their performance verified before use. An out-of-calibration PAT instrument that continues to drive real-time release decisions would constitute a data integrity failure (H-004). Test verification confirms that the calibration check workflow triggers correctly and that real-time release is actually suspended when calibration status is invalid. | session-562, validation, pat, calibration, sil-3, h-004, idempotency:session562-sys-pat-qualification-018
SYS-REQ-019 | The system SHALL generate an automatic deviation record in the EBR whenever any critical process parameter exceeds its validated specification limit, linking the deviation to the affected batch, the out-of-specification measurement, the subsystem responsible, and the time of occurrence, with the record available for QA Manager review within 10 minutes of the exceedance event. | system-requirements | System Requirements |  | Test | 86 |  | Automatic deviation record generation at the point of CPP exceedance is required by ICH Q10 (Pharmaceutical Quality System) to ensure no exceedances are missed in manual batch review. The 10-minute availability target ensures the QA Manager can make a real-time batch hold decision before additional product is produced under the exceedance conditions. | session-562, validation, mes, deviation, sil-2, idempotency:session562-sys-auto-deviation-record
SYS-REQ-020 | The system SHALL maintain a cleaning status registry for every product-contact equipment item, updated in real-time as cleaning activities are performed, and SHALL prevent assignment of any equipment with an expired or unconfirmed clean status to a new batch record, providing an explicit status reason to the operator when assignment is blocked. | system-requirements | System Requirements |  | Test | 86 |  | Equipment cleaning status control is a primary H-002 cross-contamination mitigation. An equipment item with expired clean status that is inadvertently assigned to a new batch would result in potential cross-contamination without detection. Test verification confirms the assignment block is enforced across all equipment status states and the reason is communicated clearly. | session-562, validation, mes, changeover, sil-3, h-002, idempotency:session562-sys-cleaning-registry
SYS-REQ-021 | The system SHALL provide a production supervisor handover capability in the MES, enabling the outgoing supervisor to formally close their shift in the EBR with an electronic signature, documenting any in-progress deviations, out-of-specification results, and equipment status, and preventing the next shift from starting new operations until the incoming supervisor has reviewed and acknowledged the handover record. | system-requirements | System Requirements |  | Test | 86 |  | Structured shift handover with EBR documentation prevents loss of critical operational context between shifts. The Tablet Press Jam ConOps scenario occurs on night shift — unresolved deviations from the previous shift that are not formally documented at handover could result in incorrect batch disposition decisions. | session-562, validation, mes, handover, 21cfr11, idempotency:session562-sys-shift-handover
SYS-REQ-022 | The Pharmaceutical Manufacturing Line SHALL be installed in a GMP-compliant facility comprising a minimum of four classified cleanrooms: a weigh booth (ISO 7 / Grade C), a granulation and compression area (ISO 8 / Grade D), a coating and packaging area (ISO 8 / Grade D), and a quality control laboratory; with an equipment footprint not exceeding 800 m² and physical access controlled by HVAC pressure cascade and electronic interlocks. | system-requirements | System Requirements |  | Inspection | 86 |  | Physical facility and layout constraints for the manufacturing line are required by EU GMP Annex 1 and FDA 21 CFR Part 211 to ensure product quality, containment, and cleanroom classification are maintained. The specification of classified rooms and controlled access is not derivable from functional requirements alone and must be explicitly stated to support facility qualification activities. | session-565, facility, physical-layout, lint-fix-lh3, idempotency:ses565-mfg-line-physical-layout, idempotency:ses565-mfg-line-physical-layout
SYS-REQ-023 | While in Normal Production mode, the system SHALL provide an operator override capability allowing a qualified Production Supervisor or QC Analyst to suspend automated batch diversion, IPC rejection, or PAT-triggered alarms, subject to mandatory electronic signature per 21 CFR Part 11, a maximum override duration of 60 minutes before automatic restoration, and audit trail entry recording the operator identity, override reason, and duration. | system-requirements | System Requirements |  | Test | 86 |  | Normal production mode executes batch logic semi-autonomously; any autonomous control system operating in a regulated pharmaceutical environment must have a defined human-in-the-loop override per FDA guidance on computer-aided manufacturing and IEC 61508 requirements for Functionally Autonomous systems with SIL classification. The 60-minute limit prevents indefinite bypass of safety functions while allowing short-term operational decisions. | session-565, normal-production, override, functionally-autonomous, lint-fix-lh4, lint-fix-lh8, idempotency:ses565-np-mode-override, idempotency:ses565-np-mode-override
SYS-REQ-025 | The physical sensors and instruments implementing environmental monitoring during normal production SHALL be mounted within the manufacturing line cleanroom bays, with differential pressure transmitters installed at each controlled room boundary, temperature and humidity probes at product exposure height, and all sensor housings constructed from 316L stainless steel meeting ISO 8 cleanroom installation standards. | system-requirements | System Requirements |  | Inspection | 86 |  | Specifying the physical location and construction of sensors implementing the normal production environmental monitoring requirement (SYS-REQ-006) is needed to support facility qualification documentation. Physical embodiment of the monitoring function during normal production must be defined separately from the functional monitoring requirement. | session-565, normal-production, sensors, physical-embodiment, idempotency:ses565-np-sensors-v2, idempotency:ses565-np-sensors-v2
SYS-REQ-026 | The system SHALL provide a dedicated physical cleanroom monitoring network comprising calibrated differential pressure transmitters (range 0–100 Pa, accuracy ±1 Pa), temperature transmitters (range 15–30°C, accuracy ±0.3°C), and relative humidity transmitters (range 30–70% RH, accuracy ±2% RH), wired to the Environmental Control Subsystem PLC via 4–20 mA loops, with all instruments calibrated against ISO 17025-accredited standards at intervals not exceeding 12 months. | system-requirements | System Requirements |  | Test | 86 |  | SYS-REQ-006 requires continuous monitoring of cleanroom differential pressure, temperature, and humidity during Normal Production mode. This requirement defines the physical sensor infrastructure required to fulfil that monitoring obligation. EU GMP Annex 1 (Manufacture of Sterile Medicinal Products) and ISO 14644-2 (Cleanrooms and associated controlled environments — Monitoring) specify instrument accuracy requirements. The 12-month calibration interval is consistent with GMP instrument qualification norms. Resolves lint finding: 'normal production lacks Physical Object trait but has physical embodiment'. | session-, validation, cleanroom, environmental, physical-embodiment, lint-fix, idempotency:ses566-sys-cleanroom-physical-embodiment
SYS-REQ-027 | The Process Control System SHALL provide a hardware-enforced manual override capability at each equipment control panel that allows an operator to de-energise any individual equipment actuator independently of software state, and SHALL accept Emergency Stop commands from any safety relay input within 250 milliseconds regardless of software execution state or PLC program mode. | system-requirements | System Requirements |  | Test | 86 |  | The PCS is classified as Functionally Autonomous (controlling equipment without continuous human input) per EN ISO 13849-1 (Safety of machinery — Safety-related parts of control systems). Autonomous control systems require hardware-level safety overrides that cannot be defeated by software failure — IEC 61508 (Functional safety of E/E/PE safety-related systems) clause 7.4.2 requires manual overrides for SIL-2 systems. The 250ms E-stop response is the maximum reaction time that limits rundown energy in tablet press and granulator applications. This resolves the lint finding: 'process control system is Functionally Autonomous but has no safety/override constraints'. | session-566, validation, process-control-system, safety-override, lint-fix, sil-2, idempotency:ses566-sys-pcs-manual-override
SYS-REQ-028 | While in Normal Production mode, the system SHALL be housed within a GMP-compliant equipment rack or panel enclosure (IP54 or better, stainless steel housing) that physically integrates the Environmental Monitoring System controller, the SCADA PCS I/O modules, and the 4-20mA signal conditioning hardware for at least three differential pressure transmitters (weigh booth, granulation bay, coating/packaging bay boundaries), RTD temperature probes, and capacitive humidity sensors at 0.8–1.2 m above finished floor level in each classified bay; the rack SHALL be installed within the manufacturing line classified area and connected to the clean power UPS supply specified in SYS-REQ-007. | system-requirements | System Requirements |  | Inspection |  |  | Lint finding: 'normal production' concept (hex 40B53A50) lacks Physical Object trait but SYS-REQ-006 imposes physical monitoring constraints. This requirement provides the physical embodiment specification for the environmental monitoring infrastructure that executes during Normal Production mode, resolving the ontological mismatch. Derived from SYS-REQ-006 (cleanroom monitoring parameters and response times) and consistent with SYS-REQ-025 (sensor mounting) and SYS-REQ-026 (4-20mA loop infrastructure). EU GMP Annex 1 mandates continuous environmental monitoring in classified zones during production. | session-567, validation, lint-fix-lintHigh, normal-production, physical-embodiment, idempotency:session567-sys-normal-production-physical-embodiment
SYS-REQ-029 | The system SHALL implement dust explosion prevention measures compliant with ATEX Directive 2014/34/EU (Equipment and protective systems intended for use in potentially explosive atmospheres) for all enclosed powder processing equipment (granulator, mill, blender, tablet press hopper, dust extraction ducting), including continuous LEL monitoring with automatic equipment de-energisation at 25% LEL, nitrogen inerting capability for high-risk enclosures, and explosion venting or suppression on all vessels exceeding 0.1 m³ volume. | system-requirements | System Requirements |  | Test |  |  | H-003: Fine pharmaceutical powder (API and excipient particles <100um) in enclosed equipment with ignition sources (motors, static discharge, hot surfaces) creates a dust explosion hazard. ATEX Directive 2014/34/EU mandates equipment classification and protection measures. The 25% LEL trigger provides a 4:1 safety margin per EN 14034. Nitrogen inerting reduces oxygen below the Limiting Oxygen Concentration. SIL 2 allocation reflects catastrophic severity with rare frequency. | system, sil-2, h-003, safety, session-2, idempotency:sys-pharma-dust-explosion-h003-2
SYS-REQ-030 | The Process Control System (PCS) network SHALL be isolated from enterprise IT networks by a firewall or unidirectional security gateway, implementing network segmentation per IEC 62443-3-3 (Industrial communication networks — IT security) Security Level 2, with no direct internet connectivity, and SHALL enforce role-based access control with individual user authentication for all HMI and engineering workstation access. | system-requirements | System Requirements |  | Inspection |  |  | The PCS executes SIL-2 safety functions (LOTO enforcement per SYS-REQ-016) and controls potent compound containment (SYS-REQ-004). Cyber intrusion could bypass safety interlocks, release hazardous compounds, or corrupt batch records. IEC 62443-3-3 SL-2 provides the minimum mitigations for industrial control systems with potential safety consequences. Network isolation prevents lateral movement from enterprise IT systems, a common OT attack vector. | session-549, qc, cybersecurity, pcs, idempotency:sys-pcs-cybersecurity-session-549
VER-REQ-001 | The verification activity for SUB-REQ-003 SHALL inject a pre-characterised reference standard tablet spectrum into the PAT DAC Workstation and confirm that CQA model evaluation completes and returns a pass/fail classification within the specified 30-second sample interval cycle. | verification-requirements | Verification Requirements |  | Test | 86 |  | SIL-3 H-004 safety function: CQA model latency directly determines how many OOS tablets pass before the diversion valve responds. The 2-second criterion bounds the number of tablets at risk between sensor acquisition and valve actuation at 60 RPM press speed (approximately 4 tablets per second) to fewer than 8 tablets, which is within the divertible buffer volume. | reqs-eng-session-555
VER-REQ-002 | The verification activity for SUB-REQ-004 SHALL apply a CQA limit-exceedance command to the Diversion Valve Assembly pneumatic solenoid at operating pressure (5-7 bar) and confirm that valve position transitions from accept to reject within 2 seconds as measured by dual limit switch feedback across 10 test actuations. | verification-requirements | Verification Requirements |  | Test | 86 |  | SIL-3 H-004 safe state: the valve must reach the reject position before the next tablet reaches the accept stream. At 60 RPM press speed, tablets exit at 1-second intervals; 500ms actuation leaves a 500ms margin. The spring-return test verifies fail-safe behaviour — the hardware safety function independent of software. | reqs-eng-session-555
VER-REQ-003 | The verification activity for SUB-REQ-005 SHALL inject a degraded NIR reference spectrum (SNR reduced by 50% via attenuation filter) into the PAT subsystem and confirm that the sensor diagnostic algorithm detects the degradation within 15 seconds and generates a sensor health alert to the DAC Workstation. | verification-requirements | Verification Requirements |  | Test | 86 |  | SIL-3 H-004: sensor degradation that is not detected means CQA model predictions are based on corrupted spectra, potentially releasing OOS product without triggering diversion. The 15-second detection window allows one to two press rotations before the operator is notified to switch to manual sampling mode. | reqs-eng-session-555
VER-REQ-004 | The verification activity for IFC-REQ-001 SHALL inject 100 consecutive simulated CQA limit-exceedance events at the PAT DAC Workstation OPC-UA server, measure the alarm transit time to confirmed receipt at the MES OPC-UA client, and confirm that all 100 events arrive within 500 ms with zero loss. | verification-requirements | Verification Requirements |  | Test | 86 |  | SIL-3 H-004 interface criticality: the CQA alarm is the trigger for MES to confirm diversion and lock the batch record. If the alarm is lost or delayed beyond 500ms, OOS product may enter the accept stream. The 1000-event soak test detects intermittent OPC-UA subscription failures that may not appear in short tests. | reqs-eng-session-555
VER-REQ-005 | The verification activity for IFC-REQ-003 SHALL measure, following receipt of a CQA alarm from the PAT subsystem, the elapsed time for the MES to transmit a diversion acknowledgment and operator disposition to the PAT DAC Workstation, and confirm transmission completes within the specified interface latency for 20 consecutive alarm events. | verification-requirements | Verification Requirements |  | Test | 86 |  | SIL-3 H-004 interface: the acknowledgment confirms to the PAT system that the MES has registered the diversion event and locked the relevant batch record segment. Without this confirmation, the PAT system cannot determine whether a second CQA exceedance is a new event or a duplicate of the unacknowledged prior alarm. | reqs-eng-session-555
VER-REQ-006 | The verification activity for SUB-REQ-008 SHALL attempt to execute each of the five 21 CFR Part 11 critical EBR actions (batch initiation, exception handling, parameter override, batch release, deviation closure) without providing valid electronic credentials, and confirm that the MES rejects all five attempts without committing any record. | verification-requirements | Verification Requirements |  | Test | 86 |  | SIL-2 H-006 data integrity: unsigned EBR entries are inadmissible as evidence in FDA inspection and can result in consent decree or product recall. The 100% rejection criterion is absolute — no partial authentication tolerance exists under 21 CFR Part 11.50. | reqs-eng-session-555
VER-REQ-007 | The verification activity for SUB-REQ-011 SHALL apply a maintenance lock to the rotary tablet press entry in the MES LOTO registry and confirm that subsequent equipment restart commands issued via operator HMI and programmatic API are both rejected with an interlock alarm until the lock is formally removed. | verification-requirements | Verification Requirements |  | Test | 86 |  | SIL-2 H-007 mechanical entrapment: the LOTO restart prevention is the primary software barrier preventing a maintenance technician from being caught in moving equipment. The test must exercise the OPC-UA programmatic path — not only the HMI path — because PLC restart commands may bypass the HMI in some process recovery sequences. | reqs-eng-session-555
VER-REQ-008 | The verification activity for SUB-REQ-010 SHALL write 500 sequential EBR entries via the MES API, run the hash chain integrity verification job, confirm no discontinuities, then modify one mid-chain record directly and confirm the MES detects the discontinuity and generates an integrity alert within 60 seconds. | verification-requirements | Verification Requirements |  | Test | 86 |  | SIL-2 H-006: the SHA-256 hash chain is the technical control proving EBR entries have not been altered post-signature. The tamper detection test must use direct database manipulation rather than API manipulation because 21 CFR Part 11 treats database-level tampering as the primary threat model for electronic records. | reqs-eng-session-555
VER-REQ-009 | The verification activity for the end-to-end PAT-to-diversion chain SHALL measure total latency from spectrum injection at the NIR spectrometer through CQA model evaluation, OPC-UA alarm to MES, MES diversion acknowledgment, and Diversion Valve Assembly confirmed actuation, and confirm the cumulative chain latency is within the SIL-3 H-004 limit for 5 consecutive test runs. | verification-requirements | Verification Requirements |  | Test | 86 |  | The end-to-end test is the definitive SIL-3 H-004 safety case evidence. Individual component tests confirm subsystem compliance but do not demonstrate that the chain functions correctly under realistic load conditions. The 3-second total budget combines the 2-second model evaluation bound plus 500ms alarm transmission plus 500ms valve actuation margin. | reqs-eng-session-555
VER-REQ-010 | The verification activity for SUB-REQ-002 SHALL scan a certified reference material (polystyrene NIST SRM 1921b) using the Raman spectrometer and confirm that the instrument acquires a full spectrum covering the 200–3200 cm-1 range with spectral resolution ≤4 cm-1 at the 30-second specified interval. | verification-requirements | Verification Requirements |  | Test | 86 |  | Raman spectrometer performance verification confirms the instrument meets specification for blend uniformity monitoring. NIST-traceable reference materials provide measurement traceability required for GxP instrument qualification (IQ/OQ). | reqs-eng-session-555
VER-REQ-011 | The verification activity for SUB-REQ-007 SHALL measure a certified glass bead reference standard (NIST SRM 1018c, D50 = 57 µm ±3%) using the laser diffraction analyser with dry dispersion at 0.5 bar, and confirm the measured D10/D50/D90 values are within the certified tolerance band in 5 consecutive measurements. | verification-requirements | Verification Requirements |  | Test | 86 |  | Laser diffraction qualification confirms the instrument meets specification for granulation endpoint monitoring. D50 accuracy within 5% is the ICH Q8 acceptance criterion for particle size measurement in granulation development; repeatability RSD <2% meets GAMP 5 Category 3 instrument qualification requirements. | reqs-eng-session-555
VER-REQ-012 | The verification activity for SUB-REQ-015 SHALL simulate an EBR data integrity failure by injecting a hash chain discontinuity and confirm that the MES transitions operators to paper-backup recording mode within 30 minutes, that paper backup records are available to operators within 5 minutes of the alert, and that recovery to electronic recording is possible from the last verified backup. | verification-requirements | Verification Requirements |  | Demonstration | 86 |  | SIL-2 H-006 safe state: when electronic records cannot be guaranteed tamper-evident, GMP requires a fallback to paper records to maintain the manufacturing record continuity required for batch release. The 30-minute window reflects the EU GMP Annex 11 requirement for backup systems to be available promptly. | reqs-eng-session-555
VER-REQ-013 | The verification activity for IFC-REQ-006 SHALL connect a calibrated NIR reference spectrometer in parallel with the FBD in-line probe, inject 10 pre-characterised reference spectra spanning the LOD validation range (0.5% to 3.5%), and confirm that the LOD values reported via the G&B subsystem interface agree with the reference within the specified tolerance. | verification-requirements | Verification Requirements |  | Test | 86 |  | IFC-REQ-006 specifies maximum 30-second spectral data intervals and 5-second CQA model evaluation latency for the G&B-to-PAT NIR interface. The parallel-reference-spectrometer test method is chosen because it provides independent ground truth for both the data values (via certified reference spectra) and the timing (via synchronized timestamps). If this interface has latency >5 seconds under load, the PAT system receives stale LOD values and may issue false blend-endpoint signals — potentially releasing under-dried granulate with LOD above target into the IBC blender. | reqs-eng-session-555
VER-REQ-014 | The verification activity for IFC-REQ-007 SHALL trigger a simulated G&B batch start in the MES and measure the elapsed time from MES step initiation signal to PLC setpoint receipt confirmation at the HSG, FBD, and IBC Blender PLCs, confirming all three PLCs acknowledge within the specified interface response time. | verification-requirements | Verification Requirements |  | Test | 86 |  | Integration test to verify MES-to-G&B recipe delivery latency and EBR feedback interval under production load conditions. | reqs-eng-session-555
VER-REQ-015 | The verification activity for the end-to-end Granulation and Blending cycle SHALL load a validated product recipe into the MES, execute one complete G&B cycle from API powder charge to IBC seal, and confirm granulation endpoint, drying LOD within specification, sized granule D90 ≤ 1 mm, blend RSD ≤ 5.0% across stratified samples, and complete MES batch record with all IPC entries. | verification-requirements | Verification Requirements |  | Test | 86 |  | End-to-end integration test verifying the complete G&B process train produces granules meeting all CQA specifications under recipe control. This test is the minimum viable verification for GMP process validation (PV Stage 2) sign-off of the G&B subsystem. | reqs-eng-session-555
VER-REQ-016 | The verification activity for IFC-REQ-008 SHALL complete a G&B cycle producing a sealed IBC, inspect the tamper-evident seal, and confirm that the MES batch genealogy record contains the IBC mass, blend authorisation code, and lot number linking the IBC to its input raw material charges. | verification-requirements | Verification Requirements |  | Inspection | 86 |  | IBC handoff integrity is verified by inspection of the seal and genealogy record, with a negative test (blocked press start) confirming the MES access control. This matches the regulatory requirement for documented batch record evidence (21 CFR 211.182). | reqs-eng-session-555
VER-REQ-017 | The verification activity for IFC-REQ-002 SHALL inject an NIR reference degradation (40% signal attenuation) while the PAT subsystem is in nominal operation, and confirm that the MES receives an OPC UA sensor health update indicating degraded status within 10 seconds of the attenuation event. | verification-requirements | Verification Requirements |  | Test | 86 |  | IFC-REQ-002 is the primary early-warning signal for the PAT-MES CQA diversion path. Verification requires injecting a controlled degradation to confirm the OPC UA publish cycle, field completeness, and state machine transition. Failure to verify this interface could allow undetected sensor drift to produce undetected quality deviations in product. | reqs-eng-session-555
VER-REQ-018 | The verification activity for IFC-REQ-004 SHALL log MES CQA data receipt timestamps against PAT OPC UA publish timestamps during a simulated production run, inject a known OOS API concentration sample, and confirm the diversion decision is transmitted to the MES within the specified interface latency. | verification-requirements | Verification Requirements |  | Test | 86 |  | IFC-REQ-004 is the real-time CQA measurement stream that drives diversion decisions. End-to-end latency of the MES OPC UA subscription must be verified under live production protocol to confirm diversion is triggered within the 2-second hard limit before non-conforming material passes the diversion valve. This is the safety-critical data path for batch release. | reqs-eng-session-555
VER-REQ-019 | The verification activity for SUB-REQ-009 SHALL attempt to modify a completed EBR field via direct database access and via the MES UI, and confirm in both cases that the hash chain invalidation is detected and a tamper alert is generated within 60 seconds without the modification being accepted. | verification-requirements | Verification Requirements |  | Test | 86 |  | SUB-REQ-009 implements the 21 CFR Part 11 (Electronic Records; Electronic Signatures) requirement for tamper-evident records. This is a regulatory compliance test: FDA expects evidence that the hash chain integrity mechanism actually detects record modification. Pass/fail determines whether the batch release system meets 21 CFR Part 11 Subpart B Section 11.10(e) audit trail requirements. | reqs-eng-session-555
VER-REQ-020 | The verification activity for SUB-REQ-020 SHALL complete a validation blending run using placebo granules with tracer API equivalent, collect 10 stratified samples from IBC discharge points after blend-endpoint indication, and confirm that API content RSD across all samples is ≤5.0%. | verification-requirements | Verification Requirements |  | Test | 86 |  | SUB-REQ-020 sets the blend uniformity acceptance criterion for IBC blending. ICH Q2(R1) (Validation of Analytical Procedures: Text and Methodology) requires offline HPLC confirmation of the NIR endpoint model during process validation. The 10-sample stratified plan is the minimum statistical design that detects a pattern-based segregation within the IBC at 95% confidence. Failure of this test would require revalidation of the blend process. | reqs-eng-session-555
VER-REQ-021 | The verification activity for SUB-REQ-001 SHALL configure the NIR spectrometer for the 900–1700 nm range with 256-channel resolution, record 100 consecutive spectra during a simulated production run, and confirm all spectra are acquired at the 30-second interval with signal-to-noise ratio meeting the diagnostic acceptance criterion. | verification-requirements | Verification Requirements |  | Test | 86 |  | SUB-REQ-001 defines the minimum spectral parameters of the NIR spectrometer as the primary CQA sensor. Verification of spectral range and channel count ensures the PLS chemometric model built for this instrument remains valid under the as-deployed configuration. A failure here would require re-validation of the entire NIR calibration model before the instrument can be used for batch release decisions. | reqs-eng-session-555
VER-REQ-022 | The verification activity for IFC-REQ-009 SHALL trigger a PAT degraded-mode transition by disabling the NIR sensor in a simulated production environment, measure the elapsed time from mode transition to MES command receipt at the PAT subsystem, confirm continuity of CQA monitoring on the remaining active sensor channels throughout the transition, and verify that the MES manual sampling schedule command is issued within 30 seconds of degradation detection. Pass criterion: (a) MES degraded-mode command received by PAT subsystem within 30 seconds; (b) ≥1 CQA evaluation completed on each remaining active channel during the transition interval; (c) manual sampling schedule issued with 15-minute interval and sample point specification. | verification-requirements | Verification Requirements |  | Test | 86 |  | IFC-REQ-009 adds quantified performance thresholds to the degraded mode MES-PAT protocol. The 30-second MES command delivery window and CQA monitoring continuity criteria are the testable acceptance criteria for the degraded mode qualification test. Explicit pass criteria required per IEC 61508 (Functional safety of E/E/PE safety-related systems) for SIL-rated interface verification — binary pass/fail must be demonstrable. Updated per validation session 566 to resolve ambiguousReqs blocker. | reqs-eng-session-555
VER-REQ-023 | The verification activity for SUB-REQ-024 SHALL induce degradation on one NIR sensor channel, measure the elapsed time from the first degraded spectrum to suspension of CQA model evaluation on that channel, and confirm that the remaining two channels continue model evaluation throughout the suspension period. Pass criterion: suspension of the degraded channel occurs within 5 seconds of first degraded spectrum; unaffected channels maintain ≥1 CQA model evaluation per 30-second cycle throughout the test; minimum CQA throughput on remaining channels is ≥70% of nominal three-channel throughput. | verification-requirements | Verification Requirements |  | Test | 86 |  | SUB-REQ-024 quantifies response times and channel-failure thresholds for the PAT degraded-mode protocol. The 5-second suspension window and ≥70% CQA throughput retention on remaining channels are the minimum performance criteria required to assure product quality surveillance is maintained during single-channel failure. Explicit pass criteria are required so the test result is binary and auditable per EU GMP Annex 11. | reqs-eng-session-555
VER-REQ-024 | The verification activity for SUB-REQ-027 SHALL open a guard door on the Rotary Tablet Press while the press is operating at nominal speed (60 RPM), and confirm that: (a) the main drive de-energises within 200ms of guard opening as measured by current-clamp on the drive power supply; (b) the turret braking system brings turret speed to zero within 3 seconds; and (c) the MES LOTO registry logs the guard-open event with timestamp accurate to 1 second. Test shall be repeated 5 times. Pass criterion: all 5 trials meet both timing thresholds. | verification-requirements | Verification Requirements |  | Test | 86 |  | EN ISO 13849-1 (Safety of machinery: Safety-related parts of control systems) Category 3 guard interlock requires Test verification with measured response times. The 200ms and 3-second thresholds derive from the maximum kinetic energy of the turret at 60 RPM and the stopping distance required to prevent punch-tip contact with an intruding hand. | session-556, idempotency:ver-sub027-tc-loto-556
VER-REQ-025 | The verification activity for SUB-REQ-028 SHALL install a calibrated differential pressure transmitter at the Tablet Compression Containment Housing during press operation at 120 RPM, and confirm that: (a) steady-state differential pressure is maintained at -15 Pa ± 5 Pa relative to the adjacent room; (b) when a 10mm gap is simulated at the transfer sleeve, an alarm is generated within 10 seconds; and (c) the HVAC switches to 100% exhaust within 30 seconds of alarm confirmation. Pass criterion: all acceptance values met across 3 measurement cycles. | verification-requirements | Verification Requirements |  | Test | 86 |  | The -15 Pa containment threshold is derived from OEL 0.5 µg/m³ containment modelling per ISPE Good Practice Guide for Pharmaceutical Equipment Containment. Test verification is required because containment performance depends on actual airflow dynamics that cannot be confirmed by inspection or analysis alone. | session-556, idempotency:ver-sub028-tc-containment-556
VER-REQ-026 | The verification activity for IFC-REQ-010 SHALL run the rotary tablet press at 120 RPM with every-30th-tablet auto-sampling enabled, use OPC-UA monitoring software to log the IPC data stream for 30 minutes, and confirm: (a) message delivery rate ≥99.5% (measured as received messages / expected messages at 2 Hz sampling × 1800 s); (b) maximum single-message latency ≤500ms; (c) all tablet weight, hardness, and thickness values are present in each message with no null fields. Pass criterion: all three acceptance criteria met across the full 30-minute run. | verification-requirements | Verification Requirements |  | Test | 86 |  | The 99.5% delivery rate and 500ms latency limits are derived from the in-process control response time required to detect and reject out-of-specification tablets before more than 2 tablets beyond the detected outlier pass the rejection point. Test verification is mandatory because OPC-UA message delivery performance depends on actual network configuration and cannot be demonstrated by inspection. | session-556, idempotency:ver-ifc010-tc-pat-556
VER-REQ-027 | The verification activity for IFC-REQ-011 SHALL inject 50 deliberate rejection events (by commanding out-of-band force values to the IPC at 10 events/minute) and 5 operational state transitions (normal → degraded → normal → emergency stop → normal) via the test harness, and confirm: (a) each rejection event generates a corresponding rejection command to the tablet reject mechanism within 200ms; (b) each state transition event is received and displayed in the MES within 2 seconds; (c) all 55 events are recorded in the EBR with correct timestamps and event types. Pass criterion: 100% event receipt with zero dropped events and all timing thresholds met. | verification-requirements | Verification Requirements |  | Test | 86 |  | Zero-drop event delivery is required for 21 CFR Part 11 (Electronic Records; Electronic Signatures) EBR completeness — any dropped rejection event could result in a non-conforming tablet escaping to the batch. The 200ms rejection response limit is derived from tablet press throughput: at 120 RPM × 60 stations, tablets exit at 120/s, so a 200ms window allows at most 24 tablets to pass the reject point after a defect is detected. | session-556, idempotency:ver-ifc011-tc-mes-556
VER-REQ-028 | The verification activity for IFC-REQ-012 SHALL execute a simulated film coating batch cycle, logging all coating parameters (pan speed, inlet temperature, spray rate, atomisation pressure, weight gain) to the MES EBR and confirming that each parameter write completes within 60 seconds of measurement, with end-to-end data integrity confirmed by LIMS audit trail review. | verification-requirements | Verification Requirements |  | Test | 86 |  | IFC-REQ-012 requires 30-second update intervals and 60-second EBR write completion. This test validates both timing constraints under representative production load conditions, confirming that the Film Coating Subsystem to MES data channel meets GMP EBR completeness and timeliness requirements. | session-558, qc, ver, film-coating, mes, idempotency:ver-028-ifc-012-v1
VER-REQ-029 | The verification activity for IFC-REQ-013 SHALL present the Film Coating Subsystem with a compression-to-coating transfer IBC containing a complete signed transfer record, confirm the subsystem accepts the transfer and commences the coating cycle, then repeat with a second IBC containing a deliberately out-of-specification core hardness value and confirm the subsystem rejects the transfer and raises an MES alert within 30 seconds. | verification-requirements | Verification Requirements |  | Test | 86 |  | IFC-REQ-013 requires a hard reject gate at the coating subsystem boundary for out-of-specification core attributes. The pass/reject test pair validates both the acceptance and rejection paths, confirming that the inter-subsystem transfer control prevents quality-compromised material from entering the coating operation. | session-558, qc, ver, tablet-compression, film-coating, idempotency:ver-029-ifc-013-v1
VER-REQ-030 | The verification activity for IFC-REQ-014 SHALL complete a packaging line run of 1,000 serialised units, confirm 100% serial number reconciliation against the MES batch record within 5 minutes of line clearance, then simulate a line run without a valid ERP production order and confirm the MES blocks packaging start. | verification-requirements | Verification Requirements |  | Test | 86 |  | IFC-REQ-014 requires 100% serial number reconciliation within 5 minutes and MES block without production order. The 1,000-unit run provides a statistically representative sample for serialisation throughput. The production-order-absent negative test confirms the GMP authority control at packaging. | session-558, qc, ver, packaging, mes, idempotency:ver-030-ifc-014-v1
VER-REQ-031 | The verification activity for IFC-REQ-015 SHALL present the Packaging Subsystem with a film-to-packaging transfer IBC accompanied by a complete in-process release record showing all CQA attributes within specification, confirm packaging start is permitted; then repeat with a release record containing a deliberate out-of-specification coating weight gain result and confirm the Packaging Subsystem blocks line start and notifies the MES within 30 seconds. | verification-requirements | Verification Requirements |  | Test | 86 |  | IFC-REQ-015 requires a hard interlock preventing packaging without a valid release record. The dual-path test (compliant/non-compliant transfer) validates both the acceptance and blocking logic, confirming that the packaging subsystem cannot process tablets that fail coating CQA release criteria. | session-558, qc, ver, film-coating, packaging, idempotency:ver-031-ifc-015-v1
VER-REQ-032 | The verification activity for IFC-REQ-016 SHALL confirm that environmental monitoring data (temperature, RH, differential pressure, particle counts) are received in the MES at the required 5-minute intervals during a simulated production shift, then inject a simulated pressure differential exceedance signal and confirm the MES halts the affected manufacturing operation and writes an environmental deviation event to the EBR within 30 seconds. | verification-requirements | Verification Requirements |  | Test | 86 |  | IFC-REQ-016 requires a 30-second MES halt response to environmental exceedances. The timing test is critical for OEB 4/5 containment: a pressure differential loss in a potent compound area is a personnel safety event. The 30-second window must be verified under representative system load conditions to confirm the safety-critical response time is achievable. | session-558, qc, ver, containment, mes, idempotency:ver-032-ifc-016-v1
VER-REQ-033 | The verification activity for IFC-REQ-017 SHALL complete 20 consecutive dispensing operations with a calibrated balance, confirm each weighing record (material identity, actual weight, operator ID, balance calibration status) is written to the MES EBR within 60 seconds, then simulate a dispensing event with actual weight at +0.6% of target and confirm the MES records a GMP deviation event. | verification-requirements | Verification Requirements |  | Test | 86 |  | IFC-REQ-017 requires 60-second EBR write completion per dispensing event and a GMP deviation for >±0.5% weight deviation. The 20-operation run validates the timing requirement under representative throughput. The deliberate-exceedance test confirms the rejection gate at the GMP deviation threshold. | session-558, qc, ver, material-handling, mes, idempotency:ver-033-ifc-017-v1
VER-REQ-034 | The verification activity for IFC-REQ-018 SHALL present the Granulation Subsystem charge point with a correctly labelled container barcode and confirm the identity verification scan passes and charge is permitted; then present a container barcode not matching the dispensing record and confirm the subsystem rejects the charge and notifies the MES within 15 seconds. | verification-requirements | Verification Requirements |  | Test | 86 |  | IFC-REQ-018 requires a secondary identity scan at the granulation charge point to enforce the double-verification anti-mix-up protocol. The negative test (mismatched barcode) is the safety-critical path: a false-pass (allowing a wrong material into the granulator) would contaminate the entire batch. The 15-second response window is consistent with the granulation charge sequence timing. | session-558, qc, ver, material-handling, granulation, idempotency:ver-034-ifc-018-v1
VER-REQ-035 | The verification activity for IFC-REQ-019 SHALL issue a production order from the ERP test system at least 24 hours before a simulated manufacturing start, confirm the MES receives and stages the order correctly, complete a simulated batch cycle, and verify batch yield and material consumption data are returned to ERP within 4 hours of batch completion; then attempt to start manufacturing without a valid ERP production order reference in the EBR header and confirm the MES blocks the operation. | verification-requirements | Verification Requirements |  | Test | 86 |  | IFC-REQ-019 requires 24-hour advance order notification, 4-hour yield return, and an MES block without production order. These three constraints collectively enforce the GMP authority chain from ERP to MES. Each must be independently verified; the timing constraints cannot be inferred from design inspection alone. | session-558, qc, ver, erp, mes, idempotency:ver-035-ifc-019-v1
VER-REQ-036 | The verification activity for IFC-REQ-020 SHALL generate a batch sample request in the MES, confirm the LIMS receives and registers the request with correct test method and specification reference, return a passing analytical result and confirm the MES receives it within the master test schedule turnaround time; then attempt to advance batch disposition to 'released' with an outstanding LIMS result and confirm the MES blocks disposition. | verification-requirements | Verification Requirements |  | Test | 86 |  | IFC-REQ-020 requires a closed-loop LIMS-MES release workflow with the MES blocking batch disposition until all release results are received. The pass and blocking tests together validate the two critical control points: data completeness (all results received) and data quality (passing verdict required). These cannot be validated by inspection of the interface specification alone. | session-558, qc, ver, lims, mes, idempotency:ver-036-ifc-020-v1
VER-REQ-037 | The verification activity for SUB-REQ-012 SHALL apply a maintenance lock to a designated piece of equipment via the MES LOTO registry, attempt a restart command (confirming denial), remove the lock, re-attempt restart (confirming success), then attempt a lock override via the maintenance UI and confirm the system denies and logs the override attempt; all six events (lock applied, restart denied, lock removed, restart permitted, override attempted, override denied) SHALL appear in the EBR audit log with correct operator ID, equipment ID, timestamp, and outcome within 10 seconds of each event. | verification-requirements | Verification Requirements |  | Test | 86 |  | SUB-REQ-012 requires complete LOTO event logging covering all four event types. The positive-path (lock and release) tests confirm nominal logging. The override-attempt test is the safety-critical path: a false-permit on an energised machine is an H-007 mechanical entrapment hazard. SIL-2 allocation requires test-method verification, not analysis. | session-560, validation, mes, loto, sil-2, h-007, idempotency:session560-ver-037-sub012-loto-logging
VER-REQ-038 | The verification activity for SUB-REQ-014 SHALL run the MES EBR database for a simulated 4-hour production period, confirm automated backup events occur at intervals not exceeding 15 minutes by inspecting backup logs with timestamps, verify each backup file hash against the stored integrity hash; then simulate a data integrity failure by corrupting the primary EBR database, initiate restore from the most recent verified backup, and confirm full system functionality is restored within 30 minutes of failure detection, with no EBR data loss beyond the last verified backup interval. | verification-requirements | Verification Requirements |  | Test | 86 |  | SUB-REQ-014 specifies a 15-minute backup interval and 30-minute RTO. These timing requirements protect against H-006 EBR data integrity failure. The 30-minute RTO is the regulatory recovery window before a batch must be quarantined. Neither the backup interval nor the restore time can be verified by analysis of the backup architecture alone; both require measured test execution. | session-560, validation, mes, backup, sil-2, h-006, idempotency:session560-ver-038-sub014-ebr-backup
VER-REQ-039 | The verification activity for SUB-REQ-016 SHALL execute three consecutive High Shear Granulator runs using a validated placebo formulation with a characterised endpoint torque profile; inject a simulated endpoint signal (torque or NIR wet-mass spectrum at validated criterion) and measure the elapsed time from endpoint signal to granulation stop and Fluid Bed Dryer transfer initiation command, confirming the stop-and-transfer sequence completes within 10 seconds in all three runs; pass criteria: 100% of runs stop within 10 seconds, transfer initiated in all runs, endpoint event logged in EBR with timestamp. | verification-requirements | Verification Requirements |  | Test | 86 |  | SUB-REQ-016 specifies a 10-second stop-and-transfer response at granulation endpoint. Late endpoint response causes over-granulation (too dense granules), producing tablets with hardness outside specification. SIL-2 tagging requires test verification; the 10-second constraint is a real-time control loop timing requirement that cannot be demonstrated by design inspection. | session-560, validation, granulation-blending, sil-2, idempotency:session560-ver-039-sub016-hsg-endpoint
VER-REQ-040 | The verification activity for SUB-REQ-022 SHALL disable the PAT NIR blend-endpoint monitor (simulate sensor fault) mid-blending cycle, confirm the IBC blender continues for the MES-recipe fixed-time minimum duration (≥20 minutes at validated RPM) without issuing blend-complete, confirm the MES prompts for supervisory authorisation at blend time expiry and blocks blend-complete without the authorisation signature, confirm the authorised signature permits blend-complete, and verify the EBR contains a PAT-unavailable event record with timestamp and reason; then re-enable PAT and confirm normal endpoint monitoring resumes. | verification-requirements | Verification Requirements |  | Test | 86 |  | SUB-REQ-022 is the degraded-mode safety net for H-004: when PAT is unavailable, a fixed-time blend with supervisory gate prevents release of a potentially non-homogeneous batch. The supervisory authorisation gate (the safety-critical control) can only be verified by attempting blend-complete without authorisation and confirming the block. Analysis of the software design cannot substitute for this negative test. | session-560, validation, granulation-blending, pat, degraded-mode, sil-2, h-004, idempotency:session560-ver-040-sub022-degraded-blend
VER-REQ-041 | The verification activity for SUB-REQ-025 SHALL run the Rotary Tablet Press at nominal speed with instrumented punches and inject 20 deliberate out-of-range force events (±5 kN deviation from setpoint) distributed across 5 tooling stations; confirm each out-of-range tablet is rejected by the pneumatic ejector within 200 ms of ejection-point detection, confirm no in-specification tablet is incorrectly rejected, and confirm all 20 rejection events are logged in the MES batch record; then run 1,000 tablets within specification and confirm zero false rejections; pass criteria: 100% sensitivity and 100% specificity on rejection gate. | verification-requirements | Verification Requirements |  | Test | 86 |  | SUB-REQ-025 specifies a 200 ms ejection response and a ±5 kN force gate protecting product quality (H-004). A missed rejection (false negative) releases an OOS tablet; a false acceptance of a false rejection could cause a recall if it becomes systematic. The 200 ms timing requirement cannot be verified by inspection of the ejector actuator specification. Both sensitivity and specificity require physical test execution. | session-560, validation, tablet-compression, sil-2, idempotency:session560-ver-041-sub025-press-force-rejection
VER-REQ-042 | The verification activity for SUB-REQ-029 SHALL set the compression count on one punch station RFID tag to 499,999 in the test environment, cycle the press through one compression, and confirm the station count increments to 500,000 and the press halts with an RFID lifecycle limit event logged to the MES batch record; then present the press with one RFID tag read failure (tag disabled) and confirm the press does not start, the failed station is identified in the MES log, and the operator is prompted to replace the tooling station before restart; pass criteria: press halted on lifecycle limit, failed read blocks start. | verification-requirements | Verification Requirements |  | Test | 86 |  | SUB-REQ-029 protects against tooling fatigue fracture (a broken punch tip contaminating tablets with metal fragments — an H-007 and product quality risk). The lifecycle limit gate and the read-failure block are the two safety controls. Both require physical test execution with instrumented RFID state because wear accumulation and tag fault simulation cannot be analytically verified against the subsystem implementation. | session-560, validation, tablet-compression, rfid, h-007, idempotency:session560-ver-042-sub029-rfid-tooling
VER-REQ-043 | The verification activity for SUB-REQ-030 SHALL disable one of the three IPC measurement channels (weight, hardness, or thickness) while the press is running at nominal speed, confirm the press automatically reduces throughput to ≤60% of nominal RPM, confirm the MES displays a degraded-mode alert and begins prompting manual sample collection at 5-minute intervals, confirm the degraded-mode start time and failed channel are recorded in the MES batch record; then restore the failed channel and confirm the press returns to nominal throughput and MES reverts to automated IPC mode with no operator intervention required; repeat for each of the three channels. | verification-requirements | Verification Requirements |  | Test | 86 |  | SUB-REQ-030 defines the tablet compression degraded-mode safe-state (reduced speed, manual sampling) that maintains product quality when one IPC channel fails. The 60% throughput limit prevents tablet production rate from outpacing manual sampling capacity. This is a real-time control response that cannot be verified by simulation analysis; all three channel failure modes must be physically induced to confirm the subsystem correctly identifies and responds to each. | session-560, validation, tablet-compression, degraded-mode, idempotency:session560-ver-043-sub030-ipc-degraded
VER-REQ-044 | The verification activity for SYS-REQ-005 SHALL actuate the emergency stop function via operator E-stop button, automatic interlock, and software-initiated stop command in three separate test runs; measure elapsed time from trigger to de-energisation of all drive systems (pass: ≤3 s), closure of all product-transfer valves (pass: ≤5 s), and confirmed equipment standstill (pass: ≤10 s) using calibrated high-speed timers and actuator position feedback; all three activation paths must meet timing criteria in 3 consecutive runs per path. | verification-requirements | Verification Requirements |  | Test | 86 |  | SYS-REQ-005 is the system-level emergency stop safety function covering H-001 (containment breach), H-003 (dust explosion), and H-007 (mechanical entrapment). The three timing thresholds (3/5/10 s) are safety case evidence required by IEC 61508 (Functional safety of E/E/PE safety-related systems) for SIL-2 allocation. Individual subsystem stop tests (VER-REQ-024 covers press guard interlock) do not demonstrate the system-wide coordinated stop of all drives and valves in the correct sequence. This test is the definitive system-level E-stop qualification evidence. | session-561, validation, estop, sil-2, h-001, h-003, h-007, system-level, idempotency:session561-ver-sys005-estop-system-level
VER-REQ-045 | The verification activity for SYS-REQ-006 SHALL inject simulated parameter exceedances (differential pressure exceedance, temperature exceedance, humidity exceedance) sequentially in a qualified production environment and confirm: (a) MES alarm generated within 60 seconds of alert limit breach for each parameter; (b) MES-initiated production halt within 120 seconds of action limit breach; (c) each exceedance event recorded in the EBR with timestamp, parameter identity, actual value, and limit reference; test three parameter types, three consecutive runs per type, all nine runs must meet timing criteria. | verification-requirements | Verification Requirements |  | Test | 86 |  | SYS-REQ-006 specifies system-level 60-second alarm and 120-second halt response times for cleanroom environmental exceedances. H-005 (loss of cleanroom environmental control causing microbial contamination) is SIL-1. VER-REQ-032 tests only the IFC-REQ-016 pressure-differential interface; it does not verify the system-level temperature and humidity exceedance response times, nor confirm 100% EBR recording across all three environmental parameters. This system-level test is required for EU GMP Annex 1 environmental monitoring qualification and site inspection evidence. | session-561, validation, cleanroom, sil-1, h-005, system-level, envmon, idempotency:session561-ver-sys006-cleanroom-system-level
VER-REQ-046 | The verification activity for SYS-REQ-008 SHALL execute one complete product changeover sequence (cytotoxic to standard product) with a qualified operator: complete three-wash cleaning cycle guided by MES workflow, collect swab samples at all 15 predefined worst-case locations and rinse water samples, confirm MES prevents production start until all cleaning steps are electronically signed, confirm swab HPLC and TOC results are below acceptance limits, confirm MES blocks next batch record initiation until all cleaning verification signatures are complete; total elapsed time from cleaning start to MES release logged in EBR. | verification-requirements | Verification Requirements |  | Test | 86 |  | SYS-REQ-008 is SIL-3 (H-002 cross-contamination) requiring changeover cleaning to be verified with quantitative HPLC and TOC acceptance limits. IEC 61508 (Functional safety of E/E/PE safety-related systems) SIL-3 mandates Test verification — Demonstration is insufficient because it cannot inject a deliberate OOS swab failure to confirm the MES blocks production restart. The Test method requires: (a) a passing run confirming normal changeover workflow, (b) a forced OOS swab injection at location 7 (worst-case hopper weld seam) to confirm MES blocks next batch initiation, (c) pass criterion: TOC ≤500µg/L and swab residue ≤0.004µg/cm² at all 15 locations, with MES batch initiation blocked until all electronic signatures complete. | session-561, validation, changeover, cleaning, sil-3, h-002, system-level, idempotency:session561-ver-sys008-changeover-system-level
VER-REQ-047 | The verification activity for SUB-REQ-031 SHALL deploy a primary DAC Workstation and a configured hot-standby instance in a test environment, inject a simulated primary node failure, and confirm that: (a) the standby instance assumes primary control within 5 seconds as measured by timestamp of first CQA model output from standby; (b) the last CQA diversion state held by the primary is replicated to the standby without loss; (c) the diversion valve remains in its last commanded state throughout the transition; and (d) the test is repeated 3 times to confirm repeatability. Pass criterion: all 3 trials meet the ≤5 second switchover threshold with zero diversion state loss. | verification-requirements | Verification Requirements |  | Test | 86 |  | IEC 61508 (Functional safety of E/E/PE safety-related systems) SIL-3 requires Test verification (not Analysis alone) for hardware fault tolerance claims. Analysis alone cannot demonstrate that the actual hardware/software implementation achieves HFT=1 — only a live failover test with timing measurements can. This VER resolves the silWithoutVer quality gate blocker and directly validates the hazard H-004 mitigation for OOS product release. | session-562, validation, pat, sil-3, h-004, architecture, redundancy, idempotency:session562-ver-sub031-sil3-hft1-failover
VER-REQ-048 | The verification activity for SUB-REQ-006 SHALL place the PAT Subsystem in sensor-degraded state by disabling one NIR channel and confirm that: (a) real-time CQA model evaluation on that channel suspends within 15 seconds; (b) a PAT DEGRADED alert appears on the SCADA dashboard within 30 seconds; (c) the MES updates sampling interval guidance from 30-minute to 10-minute intervals; and (d) all actions are recorded in the EBR deviation log with timestamps. Pass criterion: all four confirmations met in 3 consecutive test runs. | verification-requirements | Verification Requirements |  | Test | 86 |  | SUB-REQ-006 is a degraded-mode safety requirement — test verification is required because timing of alert propagation and EBR logging depends on software state machine transitions that cannot be confirmed from design documentation. The 15-second detection and 30-second alert thresholds are the maximum acceptable delay before manual QC sampling begins. | session-562, validation, pat, degraded-mode, h-004, idempotency:session562-ver-sub006-pat-degraded-alert
VER-REQ-049 | The verification activity for SUB-REQ-013 SHALL execute a simulated 3-batch production run in the MES test environment and confirm the batch genealogy record for each batch links: (a) each raw material lot number consumed; (b) each in-process test result with equipment ID and timestamp; (c) the packaging serialisation range (first and last unit serial number); and (d) operator signatures for each critical step. Pass criterion: genealogy query returns all four data categories with no null fields for all 3 batches. | verification-requirements | Verification Requirements |  | Test | 86 |  | 21 CFR Part 11 and EU GMP Annex 11 require complete and accurate batch genealogy as a prerequisite for batch release. Inspection of design documentation cannot demonstrate that all genealogy linkages are captured and queryable — only a functional test can confirm end-to-end traceability. | session-562, validation, mes, genealogy, idempotency:session562-ver-sub013-mes-genealogy
VER-REQ-050 | The verification activity for SUB-REQ-017 SHALL execute three drying cycles with placebo granules at the product-specific LOD recipe target, collect 3 stratified samples at end of drying, and confirm: (a) all 3 samples achieve LOD at or below the recipe target by Karl Fischer titration; (b) FBD inlet air temperature remained within plus or minus 2 degrees Celsius of recipe setpoint throughout the cycle per MES log. Pass criterion: all acceptance criteria met across all 3 runs. | verification-requirements | Verification Requirements |  | Test | 86 |  | LOD reduction to target is a CQA for tablet dissolution and stability. Karl Fischer titration per USP 921 provides the reference measurement for GMP validation of the drying endpoint per ICH Q8. Test verification is required because drying performance depends on actual feed granule properties and equipment state. | session-562, validation, granulation-blending, sil-2, fbd, idempotency:session562-ver-sub017-fbd-lod-target
VER-REQ-051 | The verification activity for SUB-REQ-018 SHALL install calibrated thermocouples at FBD inlet air duct and product chamber, run three consecutive drying cycles at nominal recipe setpoint, and confirm: (a) inlet air temperature remains within plus or minus 2 degrees Celsius of setpoint for at least 95 percent of each cycle; (b) any exceedance beyond plus or minus 3 degrees Celsius triggers an MES alarm within 60 seconds; (c) the MES recipe interlock halts the cycle if temperature exceeds plus or minus 5 degrees Celsius for more than 2 consecutive minutes. Pass criterion: all criteria met across all 3 test cycles. | verification-requirements | Verification Requirements |  | Test | 86 |  | Inlet air temperature is a KPP for granule LOD and physical properties. The control band derives from the ICH Q8 validated design space. Test verification requires calibrated instrumentation because PID control loop response cannot be demonstrated by inspection of parameter settings. | session-562, validation, granulation-blending, sil-2, fbd, idempotency:session562-ver-sub018-fbd-inlet-temp
VER-REQ-052 | The verification activity for SUB-REQ-019 SHALL run a post-drying milling cycle on a representative placebo granule batch, collect a sample at mill discharge, measure particle size distribution by laser diffraction per ISO 13320, and confirm: (a) D90 of the milled granule is 500 micrometres or less; (b) fines fraction below 53 micrometres does not exceed 15 percent v/v; (c) mill parameters recorded in MES match the validated recipe. Pass criterion: all acceptance criteria met across 3 milling runs. | verification-requirements | Verification Requirements |  | Test | 86 |  | Granule particle size directly impacts tablet compressibility and dissolution rate. The D90 and fines acceptance criteria are derived from the compression process validated design space per ICH Q8. Laser diffraction per USP 429 is the reference technique for pharmaceutical granule sizing. Test verification is required because milling performance depends on actual feed properties and equipment wear. | session-562, validation, granulation-blending, sil-2, mill, idempotency:session562-ver-sub019-granule-sizing-d90
VER-REQ-053 | The verification activity for SUB-REQ-021 SHALL execute a complete granulation and blending campaign in the MES test environment and confirm: (a) the MES records the net mass of each material charge within plus or minus 0.1 percent of actual as verified against calibrated balance read-back; (b) all transfer operations are logged with source and destination container ID and transferred mass; (c) mass balance closure is within plus or minus 0.5 percent for each process step. Pass criterion: all mass records complete and mass balance within tolerance across a 3-batch test run. | verification-requirements | Verification Requirements |  | Test | 86 |  | Accurate mass recording is required for 21 CFR Part 11 complete batch record and EU GMP Annex 11 data integrity. Mass balance closure is the primary control for detecting unmeasured losses indicating contamination or dispensing errors. The 0.5 percent closure limit detects single-operator dispensing errors exceeding 0.5 percent of batch size. | session-562, validation, granulation-blending, sil-2, mass-balance, idempotency:session562-ver-sub021-gb-mass-recording
VER-REQ-054 | The verification activity for SUB-REQ-023 SHALL activate OEB 3 compound handling mode in the test environment, execute a full granulation and blending cycle, and confirm: (a) all IBC charging operations execute only when containment interlock confirms isolator docking is complete per sensor log; (b) continuous air monitoring in the G&B area remains below 0.8 times the OEL action limit throughout the campaign; (c) simulated containment breach injection at 1.0 times OEL triggers automatic halt of material transfer within 10 seconds. Pass criterion: all three criteria met in a single full-cycle test. | verification-requirements | Verification Requirements |  | Test | 86 |  | OEB 3 containment is a SIL-2 requirement addressing H-001 airborne potent compound exposure. The 10-second auto-halt threshold is derived from operator dose accumulation modelling at the OEL action limit. Test verification is mandatory because containment interlock logic depends on physical sensor states and pneumatic actuation that cannot be verified by inspection. | session-562, validation, granulation-blending, sil-2, h-001, containment, idempotency:session562-ver-sub023-gb-oeb3-containment
VER-REQ-055 | The verification activity for SUB-REQ-026 SHALL operate the Tablet In-Process Control System at nominal press speed (60 RPM), confirm auto-sampling of every 30th tablet via IPC log (sample count equals run duration in seconds times RPM times station count divided by 30, within plus or minus 5 percent), and confirm weight, hardness, and thickness measurements for each sampled tablet are transmitted to the PAT subsystem within 10 seconds of sampling. Pass criterion: sampling rate compliance and data transmission latency both met across a 60-minute run. | verification-requirements | Verification Requirements |  | Test | 86 |  | The every-30th-tablet sampling rate meets USP 905 content uniformity statistical power requirements. The 10-second data transmission limit ensures PAT model inputs are current — stale IPC data reduces CQA prediction accuracy. Test verification is required because sampling rate depends on IPC mechanical timing which cannot be verified from design drawings. | session-562, validation, tablet-compression, ipc, pat, idempotency:session562-ver-sub026-ipc-sampling-rate
VER-REQ-056 | The verification activity for the OEL/OEB containment system requirement (SYS-REQ-013) SHALL operate a production run with a potent compound simulant at OEB 4 containment conditions, inject a simulated air concentration at 80 percent of the OEL action limit into the continuous monitoring system, and confirm: (a) an alarm is generated within 30 seconds of the injection; (b) the alarm is visible on the MES SCADA operator display; and (c) the EBR deviation log records the event with a timestamp accurate to 1 second. Pass criterion: all three confirmations met. | verification-requirements | Verification Requirements |  | Test | 86 |  | SYS-REQ-013 is a SIL-2 safety requirement driving H-001 mitigation. Test verification is required to confirm the alarm propagation latency and EBR logging are consistent with actual system behaviour under simulated exposure conditions. | session-562, validation, containment, sil-2, h-001, oel, idempotency:session562-ver-sys013-oel-alarm
VER-REQ-057 | The verification activity for the process validation data recording requirement (SYS-REQ-014) SHALL execute a complete production batch from raw material dispense through packaging, export the batch EBR, and confirm using a data completeness checklist that all ICH Q8 required CPP and CQA data fields are present, timestamped, and associated with the correct batch ID. Pass criterion: zero missing mandatory data fields across a 3-batch validation run. | verification-requirements | Verification Requirements |  | Analysis | 86 |  | The appropriate verification for data completeness and format compliance is Analysis against the ICH Q8 data requirements checklist. This confirms the EBR structure meets regulatory filing requirements without requiring a live regulatory submission. | session-562, validation, process-validation, ich-q8, idempotency:session562-ver-sys014-ich-q8-data
VER-REQ-058 | The verification activity for the EU FMD serialisation requirement (SYS-REQ-015) SHALL execute a packaging line run of 100 serialised units in the EMVS test environment, confirm 100 percent of serial numbers are successfully submitted to the national medicines verification system within 24 hours, and confirm that attempting to verify a decommissioned serial number returns a decommissioned status within 5 seconds. Pass criterion: 100% successful submission and correct decommissioned status response. | verification-requirements | Verification Requirements |  | Test | 86 |  | EU Delegated Regulation 2016/161 compliance requires functional integration with the national EMVS. Test verification against the EMVS test repository is the only way to confirm correct data format and successful API communication with the external system. | session-562, validation, serialisation, eu-fmd, regulatory, idempotency:session562-ver-sys015-eu-fmd
VER-REQ-059 | The verification activity for the EN ISO 13849-1 machine safety requirement (SYS-REQ-016) SHALL perform a documented Performance Level calculation for the guard interlock, emergency stop, and LOTO verification safety functions using the methodology of EN ISO 13849-1:2015, confirm that each function achieves PLd or higher, and document MTTFd, DCavg, and CCF values for each safety function in the safety case. Pass criterion: all three safety functions confirmed at PLd in the documented calculation. | verification-requirements | Verification Requirements |  | Analysis | 86 |  | EN ISO 13849-1 PL determination is a structured analytical process, not a physical test. The PL calculation methodology using MTTFd, DCavg, and CCF per ISO 13849-1 is the accepted verification method for Machinery Directive 2006/42/EC compliance. Analysis is the correct verification type for this standards-based calculation. | session-562, validation, machine-safety, en-iso-13849, idempotency:session562-ver-sys016-iso13849-pl
VER-REQ-060 | The verification activity for the OEE tracking requirement (SYS-REQ-017) SHALL run the system for 24 hours of simulated production with known availability events (3 unplanned stops of known duration), known speed losses (2 hours at 80 percent rated speed), and known quality losses (5 percent rejected tablets), compute the expected OEE from these inputs, and confirm the system-calculated OEE is within plus or minus 2 percent of the expected value. Pass criterion: OEE calculation accuracy within tolerance and alert generated when subsystem OEE drops below 75 percent. | verification-requirements | Verification Requirements |  | Test | 86 |  | OEE calculation accuracy cannot be confirmed by inspection of the calculation algorithm alone — it requires end-to-end verification that data collection from all subsystems feeds the OEE calculation correctly. The plus or minus 2 percent tolerance is within measurement uncertainty for a 24-hour production window. | session-562, validation, oee, idempotency:session562-ver-sys017-oee
VER-REQ-061 | The verification activity for the PAT qualification enforcement requirement (SYS-REQ-018) SHALL set one PAT instrument's calibration status to expired in the MES, attempt to initiate real-time release for a batch, and confirm: (a) the MES blocks real-time release initiation with an explicit error message citing the out-of-calibration instrument; (b) the block is not bypassable without QA Manager role credentials; and (c) the calibration status and block event are recorded in the EBR. Pass criterion: all three confirmations met. | verification-requirements | Verification Requirements |  | Test | 86 |  | SYS-REQ-018 is a SIL-3 requirement addressing H-004 OOS product release. The enforcement of PAT calibration as a real-time release gate must be verified by Test — it cannot be confirmed by inspection because the block depends on runtime status flag evaluation in the MES workflow engine. | session-562, validation, pat, calibration, sil-3, h-004, idempotency:session562-ver-sys018-pat-calibration-block
VER-REQ-062 | The verification activity for the PAT power supply requirement SHALL simulate a mains power failure by switching off the PAT subsystem UPS input, confirm: (a) the PAT subsystem continues operating without interruption for a minimum of 4 hours on battery; (b) a power failure alarm is transmitted to the MES within 10 seconds of mains loss; (c) battery state-of-charge is displayed on the SCADA operator dashboard throughout the test. Pass criterion: 4-hour autonomous operation and MES alarm within 10 seconds confirmed. | verification-requirements | Verification Requirements |  | Test | 86 |  | SUB-REQ for PAT power supply directly supports SIL-3 hazard H-004 mitigation. The 4-hour UPS runtime must be verified by actual battery discharge test — design specifications for UPS capacity cannot substitute for a live runtime test under actual load conditions. | session-562, validation, pat, power, sil-3, idempotency:session562-ver-pat-power-ups-runtime
VER-REQ-063 | The verification activity for the PAT manual override requirement SHALL log in as QC Analyst role in the MES test environment, trigger a CQA limit violation, activate the manual override function, confirm: (a) the override is accepted and recorded in the EBR within 60 seconds with operator ID and justification text; (b) attempting the same override with Operator role (below QC Analyst) is rejected; and (c) the override event is flagged in the batch audit trail for QA Manager review. Pass criterion: all three confirmations met. | verification-requirements | Verification Requirements |  | Test | 86 |  | The manual override is a SIL-3 safety function — it must be restricted to qualified personnel and fully audit-trailed. Test verification is required because role-based access control enforcement depends on runtime identity and authorisation logic that cannot be confirmed by inspection of configuration settings alone. | session-562, validation, pat, override, sil-3, h-004, idempotency:session562-ver-pat-override-rbac
VER-REQ-064 | The verification activity for the MES watchdog timer requirement SHALL stop the EBR processing heartbeat in the test environment, wait 95 seconds (3 consecutive missed heartbeats at 30-second interval), and confirm: (a) a system health alert is logged to the CMMS within 100 seconds; (b) the SCADA operator display changes to system-unavailable state within 100 seconds; (c) a new batch record initiation attempt fails with an explicit system-unavailable error. Pass criterion: all three confirmations met. | verification-requirements | Verification Requirements |  | Test | 86 |  | The MES watchdog is a SIL-2 autonomous system safety control. Test verification is required because watchdog timer logic depends on actual heartbeat timing and state machine transitions — design documentation review cannot confirm the watchdog fires correctly under real failure conditions. | session-562, validation, mes, watchdog, sil-2, h-006, idempotency:session562-ver-mes-watchdog-test
VER-REQ-065 | The verification activity for the Emergency Stop recovery requirement SHALL trigger a simulated containment breach alarm, confirm the system enters Emergency Stop mode, then attempt re-energisation without QA Manager sign-off and confirm rejection, then wait 30 minutes, perform QA Manager EBR sign-off, and confirm production equipment is permitted to restart. Pass criterion: unauthorised re-energisation blocked and authorised re-energisation permitted after sign-off and clearance period. | verification-requirements | Verification Requirements |  | Test | 86 |  | Emergency Stop mode exit is a SIL-2 safety gate for H-001 and H-007 hazards. Test verification of the QA sign-off enforcement is mandatory — the effectiveness of an access control gate cannot be demonstrated by inspection of the workflow configuration. The 30-minute clearance period and QA sign-off requirement are both testable pass/fail criteria. | session-564, validation, emergency-stop, mode-coverage, sil-2, h-001, ambiguity-fixed
VER-REQ-066 | The verification activity for the Maintenance LOTO display requirement SHALL apply a LOTO lock to the rotary tablet press via the MES LOTO registry, attempt to power on the press via all three command interfaces (operator HMI, PLC direct command, and MES remote command), confirm all three are rejected, and confirm the LOTO status (locked, applied-by, time-applied) is displayed on the MES operator HMI. Pass criterion: all three command rejections confirmed and LOTO status correctly displayed. | verification-requirements | Verification Requirements |  | Test | 86 |  | The LOTO display and enforcement during Maintenance mode is a SIL-2 safety requirement for H-007 prevention. OSHA 29 CFR 1910.147 requires energy control procedures to be verified — inspection of LOTO registry configuration alone cannot demonstrate that all three command paths are blocked. Testing all three command paths is critical because single-channel protection is insufficient for SIL-2. | session-562, validation, maintenance, loto, sil-2, h-007, idempotency:session562-ver-maintenance-loto-display
VER-REQ-067 | The verification activity for the Degraded Production mode real-time release block requirement SHALL activate degraded production mode in the MES test environment, produce a test batch, and confirm: (a) real-time release initiation is blocked with an explicit degraded-mode error message within 2 seconds of initiation attempt; (b) the batch is placed in quarantine status automatically within 60 seconds of batch completion; (c) QA Manager EBR sign-off is required before the batch is permitted to advance from quarantine. Pass criterion: all three confirmations met in 3 consecutive test runs; zero false-pass events (real-time release must never succeed in degraded mode). | verification-requirements | Verification Requirements |  | Test | 86 |  | Blocking real-time release in degraded mode is an H-004 mitigation. The 2-second block response time and 60-second quarantine automation deadline are the minimum performance criteria required for this test to be meaningful. Zero false-pass events (real-time release succeeding in degraded mode) is the absolute safety criterion. Three consecutive runs confirm the control is not intermittent. Numeric criteria added per validation session 566. | session-564, validation, degraded, sil-3, h-004, rtrt, ambiguity-fixed
VER-REQ-068 | The verification activity for the Tablet Compression Subsystem power supply requirement SHALL measure the main drive de-energisation time from EPO activation using a current clamp and oscilloscope, confirm de-energisation within 200ms across 5 test actuations, and confirm the MES LOTO registry logs the EPO event with a timestamp within 1 second of actuation. Pass criterion: all 5 actuations within 200ms and MES log entry confirmed. | verification-requirements | Verification Requirements |  | Test | 86 |  | The 200ms EPO response is a direct contributor to H-007 safe state (equipment de-energised). Measurement of actual de-energisation time by oscilloscope is required because design specifications for contactor response times have manufacturing tolerances that may result in slower actual response. The MES LOTO log entry is required for 21 CFR Part 11 audit completeness. | session-562, validation, tablet-compression, power, h-007, idempotency:session562-ver-tc-epo-timing
VER-REQ-069 | The verification activity for the Granulation and Blending Subsystem power supply requirement SHALL measure supply voltage at the HSG and FBD main distribution boards during a nominal production cycle, confirm voltage remains within plus or minus 10 percent of 400V nominal, inject a simulated voltage deviation beyond 10 percent, and confirm an MES alarm is generated within 60 seconds. Pass criterion: voltage within tolerance during production and alarm within 60 seconds of simulated deviation. | verification-requirements | Verification Requirements |  | Test | 86 |  | Power supply voltage deviation affects both the HSG impeller speed (granule endpoint CQA) and FBD heating performance (LOD CQA). Test verification requires actual voltage measurement at distribution boards — design specifications cannot account for cable voltage drops and transformer loading effects in the installed facility. | session-562, validation, granulation-blending, power, idempotency:session562-ver-gb-power-voltage
VER-REQ-070 | The verification activity for the Film Coating Subsystem power supply requirement SHALL run a complete simulated coating batch cycle, log MES power consumption data for the cycle, confirm power consumption per batch is within plus or minus 15 percent of the design specification value, and confirm the EPO de-energises all drives within 500ms across 5 test actuations. Pass criterion: power consumption within tolerance and EPO timing confirmed. | verification-requirements | Verification Requirements |  | Test | 86 |  | Film coating power consumption logging is required for OEE calculation accuracy. The 15 percent tolerance accounts for coating load variability across batches. EPO test is required for H-001 safe state confirmation during coating of potent compounds. | session-562, validation, film-coating, power, idempotency:session562-ver-fc-power-consumption
VER-REQ-071 | The verification activity for the Containment and Environmental Control Subsystem UPS requirement SHALL disconnect mains power from the containment subsystem UPS, confirm all monitoring and alarm functions remain operational for a minimum of 2 hours, confirm HVAC dampers remain in exhaust position throughout the test (fail-secure), and confirm UPS battery state-of-charge is displayed on the SCADA operator dashboard throughout. Pass criterion: 2-hour continuous operation and fail-secure exhaust position confirmed. | verification-requirements | Verification Requirements |  | Test | 86 |  | The containment UPS runtime is a SIL-2 safety function for H-001 mitigation during power failure. Battery runtime must be verified by actual discharge test — manufacturer UPS capacity ratings do not account for actual connected load and battery ageing in the installed system. | session-562, validation, containment, power, sil-2, h-001, idempotency:session562-ver-cec-ups-runtime
VER-REQ-072 | The verification activity for the MES server hardware requirement SHALL inspect the server room physical configuration and confirm by visual inspection: (a) dual redundant PSUs installed in each server with both connected to independent circuits; (b) server room door equipped with badge access reader with logged access events; (c) server room access log retrievable from CMMS for the previous 90 days. Pass criterion: all three items confirmed by inspection. | verification-requirements | Verification Requirements |  | Inspection | 86 |  | Physical installation and access control measures for the MES server are verifiable by Inspection — they are observable physical characteristics that do not require functional testing. The 90-day access log retention directly supports 21 CFR Part 11 audit trail requirements for the physical location housing the EBR system. | session-562, validation, mes, hardware, 21cfr11, idempotency:session562-ver-mes-server-inspection
VER-REQ-073 | The verification activity for the Startup mode entry criteria requirement SHALL configure the MES test environment with one equipment qualification record expired, one PAT system suitability check failed, and one open deviation from a prior campaign, then attempt to initiate a new batch record, and confirm the MES blocks batch record initiation with an error identifying all three blocking conditions. Pass criterion: batch record initiation blocked and all three blocking conditions clearly identified in the error message. | verification-requirements | Verification Requirements |  | Test | 86 |  | Startup mode entry gate enforcement is a quality assurance control preventing production on unqualified equipment. Test verification requires injecting each blocking condition individually and in combination to confirm the MES enforcement logic is comprehensive. Inspection of workflow configuration alone cannot confirm all conditions are evaluated. | session-562, validation, startup, mode-coverage, mes, idempotency:session562-ver-startup-entry-gate
VER-REQ-074 | The verification activity for the Degraded Production mode quarantine requirement SHALL complete a production run in degraded mode, confirm: (a) the batch is automatically placed in MES quarantine status within 60 seconds of batch completion without operator action; (b) an attempt to advance the batch to released status without QA Manager sign-off is rejected within 2 seconds with an explicit error message; (c) QA Manager sign-off (electronic signature) permits batch advancement. Pass criterion: automatic quarantine within 60 seconds confirmed, QA sign-off gate enforced with zero bypass events, all three test runs pass. | verification-requirements | Verification Requirements |  | Test | 86 |  | The Degraded mode quarantine gate is an H-004 mitigation control. The 60-second automated quarantine deadline and the 2-second reject response for unauthorised release attempts are the quantified performance criteria required to confirm the control works under operational timing conditions. Zero bypass events is the absolute criterion — the sign-off gate must never fail. Numeric thresholds added per validation session 566 to resolve ambiguousReqs blocker. | session-564, validation, degraded, mode-coverage, h-004, ambiguity-fixed
VER-REQ-075 | The verification activity for SUB-REQ-048 SHALL inject a simulated airborne concentration at 85 percent of OEL into the continuous monitoring system, confirm: (a) Emergency Stop activates within 5 seconds; (b) all material transfer valves close within 5 seconds as confirmed by position feedback; (c) HVAC switches to 100 percent exhaust within 15 seconds; (d) evacuation alarm sounds at minimum 85 dB at 1 metre. Pass criterion: all 4 criteria met in 3 test runs. | verification-requirements | Verification Requirements |  | Test | 86 |  | H-001 is a SIL-2 hazard. Test verification with timing measurements is required for all four automated responses. Design analysis alone cannot confirm actual pneumatic valve actuation and HVAC damper response times match specified values. | session-562, validation, containment, sil-2, h-001, idempotency:session562-ver-sub048-breach-autoresponse
VER-REQ-076 | The verification activity for SUB-REQ-049 SHALL configure the test environment to log air monitoring data for 24 hours, confirm that a minimum of 1 sample per 60 seconds per monitoring point is recorded in the EBR log, export the 24-hour record in CSV and PDF formats, and confirm file format validity. Pass criterion: sampling frequency confirmed at 1 per 60 seconds or higher and both export formats valid. | verification-requirements | Verification Requirements |  | Test | 86 |  | Air monitoring frequency and data export format compliance cannot be confirmed by inspection of system configuration alone — actual data logging rate must be measured across a 24-hour period to confirm no gaps. Export format validation ensures regulatory inspection accessibility. | session-562, validation, containment, monitoring, h-001, idempotency:session562-ver-sub049-air-monitoring-freq
VER-REQ-077 | The verification activity for SUB-REQ-050 SHALL inject a cleaning validation failure result (location 7 swab result exceeding acceptance limit) into the MES test environment, confirm: (a) next batch associated with that equipment is automatically placed in quarantine; (b) QA Manager receives SCADA notification and email alert within 5 minutes; (c) batch release is blocked until QA Manager sign-off. Pass criterion: all 3 confirmations met. | verification-requirements | Verification Requirements |  | Test | 86 |  | Automatic quarantine on cleaning validation failure is a H-002 SIL-3 mitigation. Test verification is required to confirm the automatic quarantine trigger and dual notification path are both functional — inspection of workflow configuration cannot confirm the actual message routing and quarantine state enforcement. | session-562, validation, mes, changeover, sil-3, h-002, idempotency:session562-ver-sub050-cleaning-quarantine
VER-REQ-078 | The verification activity for SUB-REQ-051 SHALL attempt to advance an API dispensing step in the MES test environment with only one operator confirmation, confirm the step advancement is blocked, then provide both operator confirmations and confirm the step advances. Repeat with a simulated second operator confirmation from an unauthorised role and confirm rejection. Pass criterion: single-confirmation advance blocked and dual authorised-role confirmation accepted. | verification-requirements | Verification Requirements |  | Test | 86 |  | Two-person API dispensing verification is a 21 CFR Part 211 critical step control for H-002. Test verification must confirm both the enforcement of two distinct operator identities and the role authorisation requirement. These are runtime EBR workflow controls that cannot be verified by inspection. | session-562, validation, material-handling, sil-3, h-002, idempotency:session562-ver-sub051-two-person-api
VER-REQ-079 | The verification activity for SUB-REQ-052 SHALL run the tablet compression line with the metal detection system active, inject 5 known metallic particles of 0.5mm diameter into the tablet stream at known positions, confirm: (a) all 5 particles are detected; (b) rejection mechanism activates and diverts the 10 tablets before and 10 after each detected particle; (c) a critical alarm is generated in the MES for each detection. Pass criterion: 100 percent detection rate and correct rejection window confirmed. | verification-requirements | Verification Requirements |  | Test | 86 |  | Metal detection performance cannot be verified by equipment specification review alone — actual detection sensitivity depends on tablet mass, line speed, and detector calibration. Testing with 0.5mm particles at known positions confirms the worst-case detection scenario for the punch-tip fragment size most likely to result from tooling breakage. | session-562, validation, tablet-compression, metal-detection, idempotency:session562-ver-sub052-metal-detection
VER-REQ-080 | The verification activity for SUB-REQ-053 SHALL connect a calibrated dust concentration monitor to the FBD exhaust duct, inject a dust aerosol to reach 30 percent of LEL, confirm: (a) the system detects concentration above 25 percent LEL threshold; (b) nitrogen inerting activates within 10 seconds; (c) FBD airflow reduces to minimum circulation rate within 10 seconds; (d) SIL-2 alarm is generated in MES within 10 seconds. Pass criterion: all 4 criteria met. | verification-requirements | Verification Requirements |  | Test | 86 |  | H-003 dust explosion prevention is a SIL-2 safety function. Test verification with a calibrated dust monitor and timed response measurement is required. The 25 percent LEL detection threshold and 10-second response time must be confirmed under actual process conditions — design specifications for sensor sensitivity and pneumatic valve response times may differ from installed performance. | session-562, validation, granulation-blending, dust-explosion, sil-2, h-003, idempotency:session562-ver-sub053-dust-lel
VER-REQ-081 | The verification activity for SUB-REQ-054 SHALL run 500 blister packs through the packaging vision inspection system, introduce 10 packs with deliberate defects (5 absent tablets, 3 broken tablets, 2 foreign particle simulants) at known positions, confirm: (a) all 10 defective packs are rejected; (b) no non-defective packs are rejected; (c) all rejected pack IDs and rejection reasons are logged in the EBR. Pass criterion: 100 percent defect detection with zero false rejects and complete EBR logging. | verification-requirements | Verification Requirements |  | Test | 86 |  | Vision inspection at 100 percent confidence is a final critical quality gate before product release. Test verification with known defect types and zero false-reject tolerance is required because vision system performance depends on lighting, tablet colour, and line speed factors that vary with product. The EBR logging requirement ensures rejected pack traceability for batch disposition. | session-562, validation, packaging, vision-inspection, idempotency:session562-ver-sub054-vision-inspection
VER-REQ-082 | The verification activity for SUB-REQ-055 SHALL register a time-critical sample request in the MES, confirm the LIMS receives the request within 30 seconds, enter the result in LIMS, and confirm the MES displays the result within 5 minutes of LIMS entry. Also confirm that a rejected result is retained with rejection reason in both systems. Pass criterion: both latency SLAs met and rejected result retained in both audit trails. | verification-requirements | Verification Requirements |  | Test | 86 |  | LIMS-MES integration latency determines real-time release cycle time. The 30-second receipt and 5-minute result return SLAs must be verified by end-to-end integration test — interface configuration review cannot confirm actual network latency and system processing time under production load conditions. | session-562, validation, lims, mes, idempotency:session562-ver-sub055-lims-mes
VER-REQ-083 | The verification activity for SUB-REQ-056 SHALL complete a simulated batch, confirm the MES generates a PDF/A batch review report within 15 minutes of batch completion, verify the report contains all required sections (CPP trends, IPC results, deviation summary, compliance checklist), and confirm the PDF/A format is valid per ISO 19005 using a PDF/A validator. Pass criterion: report generated within 15 minutes and PDF/A format confirmed valid. | verification-requirements | Verification Requirements |  | Test | 86 |  | Batch review report SLA and PDF/A format compliance must be verified by a functional end-to-end test. The 15-minute SLA is a business process requirement for same-shift review. PDF/A validity requires format-level testing with a standards-compliant validator — design review cannot confirm PDF/A compliance in the generated output. | session-562, validation, mes, batch-review, idempotency:session562-ver-sub056-batch-report
VER-REQ-084 | The verification activity for SUB-REQ-057 SHALL operate the PAT subsystem for 31 days in the test environment, query the audit log for day 1 entries and confirm they are present and unmodified, attempt to modify a log entry and confirm rejection, and export the full 30-day record in CSV format and confirm all entries are present. Pass criterion: 30-day retention confirmed, tamper evidence confirmed, and export validated. | verification-requirements | Verification Requirements |  | Test | 86 |  | The 30-day PAT audit log retention is a SIL-3 H-004 data integrity control. Tamper-evidence verification requires attempting a modification and confirming it is rejected — inspection of technical controls alone cannot confirm tamper-evidence effectiveness. The CSV export confirmation is required for regulatory inspection accessibility. | session-562, validation, pat, audit-log, sil-3, h-004, idempotency:session562-ver-sub057-pat-audit-log
VER-REQ-085 | The verification activity for the auto-deviation record requirement (SYS-REQ-019) SHALL inject a CPP limit exceedance into the test system, confirm a deviation record is created in the EBR within 10 minutes linking all required data fields (batch ID, measurement value, subsystem, timestamp), and confirm the deviation is visible to QA Manager in the SCADA review queue within the same window. Pass criterion: complete deviation record within 10 minutes. | verification-requirements | Verification Requirements |  | Test | 86 |  | Deviation record generation latency must be confirmed by functional test because it depends on real-time EBR write performance under production load. The 10-minute SLA is a patient safety and regulatory compliance requirement under ICH Q10. | session-562, validation, mes, deviation, idempotency:session562-ver-sys019-auto-deviation
VER-REQ-086 | The verification activity for the cleaning status registry requirement (SYS-REQ-020) SHALL set equipment item A's cleaning status to expired in the MES test environment, attempt to assign equipment A to a new batch record, confirm the assignment is blocked with an explicit status reason, then complete a cleaning record for equipment A, confirm the status updates to confirmed clean, and confirm the assignment now succeeds. Pass criterion: block enforced on expired status and unblocked after cleaning confirmation. | verification-requirements | Verification Requirements |  | Test | 86 |  | Cleaning registry enforcement is a SIL-3 H-002 mitigation. Test verification confirms the enforcement gate is functional across the full status lifecycle (expired, cleaning in progress, confirmed clean). Runtime state evaluation cannot be confirmed by inspection of database schema design. | session-562, validation, changeover, sil-3, h-002, idempotency:session562-ver-sys020-cleaning-registry
VER-REQ-087 | The verification activity for the shift handover requirement (SYS-REQ-021) SHALL simulate a shift end with 1 open deviation and 1 in-progress batch, confirm the outgoing supervisor electronically signs the handover record with all required data fields, attempt to start a new production operation without incoming supervisor acknowledgement and confirm rejection, then complete incoming supervisor acknowledgement and confirm the operation is permitted to proceed. Pass criterion: operation rejection confirmed before acknowledgement and permitted after. | verification-requirements | Verification Requirements |  | Test | 86 |  | Shift handover enforcement is a 21 CFR Part 11 process control. Test verification confirms the MES workflow gate is enforced correctly for the specific scenarios where handover is most critical — active deviations and in-progress batches. Design review of workflow configuration cannot confirm runtime gate enforcement. | session-564, validation, mes, handover, ambiguity-fixed
VER-REQ-088 | The verification activity for the system-level OEE tracking (SYS-REQ-017) SHALL confirm the OEE dashboard is accessible from the SCADA operator display, that all three OEE components (Availability, Performance, Quality) are displayed with the contributing subsystem breakdown, and that an alert is generated and visible on the dashboard when a subsystem OEE drops below 75 percent for more than one production shift. Pass criterion: dashboard accessible, all components displayed, and alert confirmed. | verification-requirements | Verification Requirements |  | Demonstration | 86 |  | OEE dashboard accessibility and display correctness is confirmed by Demonstration — a functional walkthrough of the dashboard with known input values. This complements VER-REQ-069 (OEE calculation accuracy test) by confirming the display layer and alerting logic are functional. | session-562, validation, oee, idempotency:session562-ver-oee-dashboard-demo
VER-REQ-089 | The verification activity for the batch genealogy system-level requirement (SYS-REQ-007) SHALL execute a complete production campaign (materials → packaging) for a single batch, perform a genealogy query for the finished product lot number, and confirm the returned record includes: (a) all raw material lot numbers and supplier certificates; (b) all in-process test results with subsystem IDs; (c) all deviation records and their dispositions; (d) the complete serialisation range. Pass criterion: all four genealogy components present and traceable to source records. | verification-requirements | Verification Requirements |  | Test | 86 |  | SYS-REQ-007 system-level batch genealogy is a 21 CFR Part 211 and EU GMP Annex 15 requirement. Test verification of end-to-end genealogy requires an actual production campaign to confirm all data linkages are created correctly across all subsystem interfaces. Design review of database schema cannot confirm that all subsystem integration points populate genealogy records. | session-562, validation, genealogy, 21cfr11, system-level, idempotency:session562-ver-sys007-genealogy-system
VER-REQ-090 | The verification activity for SYS-REQ-003 SHALL inject 50 pre-characterised CQA test spectra spanning 10 nominal, 10 OOS-API, 10 OOS-dissolution, 10 sensor-degraded, and 10 boundary-condition samples into the system at the PAT DAC Workstation, and confirm: (a) each spectrum is evaluated within 5 seconds; (b) OOS classification triggers automatic diversion valve actuation within 2 seconds; (c) sensor-degraded samples trigger a health alert within 15 seconds. Pass criterion: 50/50 correct decisions with all timing bounds met. | verification-requirements | Verification Requirements |  | Test | 86 |  | SYS-REQ-003 is the system-level PAT/CQA requirement covering the safety-critical chain from spectrum acquisition through diversion actuation, addressing SIL-3 H-004. A system-level test with representative sample types is required because individual subsystem tests do not confirm the integrated acquisition-evaluation-actuation chain behaves correctly end-to-end. | session-564, validation, pat, sil-3, h-004, sys-level, ambiguity-fixed, idempotency:session564-ver-sys003-pat-system-level
VER-REQ-091 | The verification activity for SYS-REQ-004 SHALL install calibrated airflow velocity probes at all access point openings of a qualified potent compound enclosure, operate the system under production conditions, inject a tracer aerosol in the enclosure headspace, and confirm: (a) inward airflow velocity is at least 0.5 m/s at all open access points; (b) continuous airborne particle monitor generates an alarm when concentration exceeds 20 percent of OEL; (c) automatic enclosure lockdown activates within 10 seconds of alarm. Pass criterion: all three measurements confirmed. | verification-requirements | Verification Requirements |  | Test | 86 |  | SYS-REQ-004 is a SIL-2 H-001 safety requirement. Test verification with physical airflow measurement is required by COSHH regulations to confirm the negative pressure isolation is effective under actual production conditions. Design analysis of HVAC specifications cannot confirm in-situ airflow velocities with production equipment in place. | session-564, validation, containment, sil-2, h-001, sys-level, idempotency:session564-ver-sys004-containment-system-level
VER-REQ-092 | The verification activity for SYS-REQ-011 SHALL register an active LOTO lockout device in the MES for three separate equipment types (tablet press, granulator, packaging line), attempt restart commands for each via operator HMI, supervisor override, and programmatic API, and confirm all nine restart attempts are rejected with LOTO interlock alarm while the lockout is active; remove each lockout device and confirm equipment restart is then permitted. Pass criterion: all 9 blocking attempts rejected and all 3 restart permits granted after LOTO removal. | verification-requirements | Verification Requirements |  | Test | 86 |  | SYS-REQ-011 is a SIL-2 H-007 safety requirement — preventing energisation of equipment during maintenance. Test verification with three equipment types and three restart methods confirms the LOTO interlock is implemented uniformly across the system, not just for the specific configurations tested at subsystem level (VER-REQ-007, VER-REQ-037, VER-REQ-066). | session-564, validation, loto, sil-2, h-007, sys-level, idempotency:session564-ver-sys011-loto-system-level
VER-REQ-093 | The verification activity for SYS-REQ-001 SHALL execute a continuous 12-hour simulated production run at the nominal recipe setpoint for a representative product, log the MES production counter at the start and end of each unit operation, and confirm: (a) cumulative tablet output at end of shift is at least 300,000 tablets; (b) MES OEE report is updated at least once per hour; (c) OEE is calculated and displayed for the shift. Pass criterion: throughput target met and hourly OEE reporting confirmed. | verification-requirements | Verification Requirements |  | Test | 86 |  | SYS-REQ-001 is the primary production capacity requirement derived from STK-REQ-001. Test verification requires a full-shift production run to confirm all subsystem throughput contributions combine to meet the system-level target; static analysis of individual subsystem rates cannot confirm dynamic bottlenecks are absent. | session-564, validation, throughput, oee, sys-level, idempotency:session564-ver-sys001-throughput-system-level
VER-REQ-094 | The verification activity for SYS-REQ-002 SHALL execute a complete batch lifecycle in the MES test environment: create an EBR, execute all lifecycle steps with electronic signatures, perform an audit trail review, confirm backup occurs within 15 minutes by checking backup timestamps, then tamper with one EBR record directly and confirm the cryptographic hash integrity check detects the alteration within 60 seconds. Pass criterion: all lifecycle operations succeed with electronic signatures, backup interval confirmed, and tamper detection triggered. | verification-requirements | Verification Requirements |  | Test | 86 |  | SYS-REQ-002 covers EBR data integrity and electronic signature enforcement under 21 CFR Part 11 and EU GMP Annex 11. The original Inspection method is insufficient for a SIL-2 H-006 data integrity requirement — Test is required to confirm the hash chain, access controls, and backup intervals function correctly under actual system load. | session-564, validation, ebr, 21cfr11, sil-2, h-006, sys-level, idempotency:session564-ver-sys002-ebr-system-level
VER-REQ-095 | The verification activity for SYS-REQ-009 SHALL induce PAT sensor-degraded mode in a running production simulation, and confirm: (a) the system switches to manual in-process testing mode within 30 seconds with a 15-minute sampling schedule; (b) production throughput is maintained at 50 percent of nominal or above for the next 30 minutes; (c) Production Supervisor receives a prominent EBR annotation within 30 seconds. Pass criterion: all three confirmations met across 3 test runs. | verification-requirements | Verification Requirements |  | Test | 86 |  | SYS-REQ-009 implements the PAT Sensor Drift ConOps scenario — degraded mode must maintain minimum throughput while protecting product quality. Test verification confirms the mode transition, throughput floor, and supervisor notification all occur within the required time bounds under actual system load. | session-564, validation, degraded-mode, pat, sys-level, pat-sensor-drift-scenario, idempotency:session564-ver-sys009-degraded-mode-system-level
VER-REQ-096 | The verification activity for SYS-REQ-010 SHALL run a packaging line production of 500 saleable units, confirm 100 percent of units receive a 2D DataMatrix barcode encoding serial number, GTIN, lot number, and expiry date, measure the barcode verification reject rate over the run and confirm it is below 0.5 percent, then confirm aggregation data for the lot is uploaded to the external serialisation system within 2 hours of line completion. Pass criterion: 100 percent barcode application, reject rate below 0.5 percent, and upload confirmed. | verification-requirements | Verification Requirements |  | Test | 86 |  | SYS-REQ-010 implements EU FMD and DSCSA serialisation requirements at system level. Test verification requires a production-representative run because barcode reject rate is a statistical metric that cannot be confirmed by inspection of the print-and-verify station in isolation from the full packaging line. | session-564, validation, serialisation, eu-fmd, sys-level, idempotency:session564-ver-sys010-serialisation-system-level
VER-REQ-097 | The verification activity for SYS-REQ-012 SHALL run the tablet press at nominal speed with IPC system active, inject 10 tablets per rejection criterion (10 overweight, 10 underweight, 10 hard, 10 soft, 10 thick, 10 thin) into the press feed, confirm all 60 out-of-specification tablets are rejected at the IPC station, then inject a sequence exceeding the L1 AV threshold of 15.0 and confirm the entire production segment is rejected. Pass criterion: 60/60 individual rejections and segment rejection confirmed. | verification-requirements | Verification Requirements |  | Test | 86 |  | SYS-REQ-012 defines the system-level tablet quality rejection criteria. Test verification with deliberate OOS samples per acceptance criterion confirms the rejection logic is implemented for all specified parameters, not just the ones tested at subsystem level. The L1 AV segment rejection is an additional system-level control not covered by individual tablet rejection tests. | session-564, validation, product-quality, ipc, sys-level, idempotency:session564-ver-sys012-product-quality-system-level
VER-REQ-098 | The verification activity for SUB-REQ-058 SHALL log in as QC Analyst in the MES test environment, trigger a CQA limit violation, activate the manual override function and confirm: (a) EBR electronic signature is required before override activates; (b) override expires automatically after 60 minutes and autonomous CQA evaluation resumes; (c) attempted override without electronic signature is rejected. Pass criterion: all three confirmations met. | verification-requirements | Verification Requirements |  | Test | 86 |  | SUB-REQ-058 is a SIL-3 H-004 safety constraint on the PAT autonomous diversion function. Test is required to confirm the signature gate, duration limit, and automatic restoration all function correctly under operational conditions. | session-564, validation, pat, sil-3, h-004, override, functional-autonomy, idempotency:session564-ver-sub058-pat-override-test
VER-REQ-099 | The verification activity for SUB-REQ-059 SHALL conduct a physical inspection of the Granulation and Blending Subsystem installation during commissioning: confirm the equipment bay is classified ISO 8 (Grade D) by environmental monitoring certificate, confirm all product-contact surfaces are 316L stainless steel by material certification, and confirm all IBC transfer connections are documented as ANSI/ISPE OEB 4-compatible by supplier certificate. Pass criterion: all three material and classification certificates present and signed by QA. | verification-requirements | Verification Requirements |  | Test | 86 |  | SUB-REQ-059 is SIL-2 tagged (G&B containment subsystem contributes to H-002 cross-contamination mitigation via OEB 4 transfer connection integrity). IEC 61508 SIL-2 requires Test verification for safety-critical installation requirements — Inspection alone cannot confirm that the sealed IBC transfer connections withstand operating pressures and do not leak fine powder. The Test method adds: (d) pneumatic pressure integrity test of each ANSI/ISPE OEB 4-compatible transfer connection at 0.7 bar dry-air for 30 seconds with zero detectable powder leakage (leak detector ≤1×10⁻⁶ mbar·L/s). Inspection checks (material certificates, environmental certificate, sensor heights) are retained as Pass criteria (a)-(c) within the same Test protocol. | session-565, validation, granulation, installation, sil-2, idempotency:session565-ver-subreq059-granulation-install
VER-REQ-100 | The verification activity for SUB-REQ-060 SHALL measure PCS power consumption at full PLC chassis load using a calibrated power analyser (confirm ≤ 500 W per chassis), then disconnect utility mains and confirm: (a) UPS sustains all PLC and HMI functions for a minimum of 30 minutes; (b) a power failure alarm appears on the SCADA operator screen within 2 seconds of mains loss; (c) supply voltage remains within 23.0–25.0 VDC throughout the test. Pass criterion: all three checks confirmed in a single test run. | verification-requirements | Verification Requirements |  | Test | 86 |  | SUB-REQ-060 specifies the PCS power integrity constraints that protect batch execution during utility interruptions. Test verification with physical mains disconnection is the only method that can confirm the 30-minute autonomy period, the 2-second alarm response, and the voltage regulation simultaneously — these are measurable performance parameters that cannot be confirmed by Inspection or Analysis alone. PCS power continuity is an enabler for the MES heartbeat (SUB-REQ-061) and the safe-state transition sequence. | session-565, validation, pcs, power, ups, idempotency:session565-ver-subreq060-pcs-power
VER-REQ-101 | The verification activity for SUB-REQ-061 SHALL: (a) Watchdog test — suspend the MES heartbeat signal in a test environment and confirm the watchdog triggers a controlled safe-state transition within 30 seconds: batch execution suspended, HVAC failsafe command issued (confirmed at HVAC controller), and an operator alert generated; (b) E-STOP test — activate the dedicated physical E-STOP button at each operator workstation in sequence and confirm all MES-controlled automated functions halt within 10 seconds per activation; (c) Confirm all watchdog and E-STOP events are recorded in the EBR with timestamp and operator station ID. Pass criterion: all activations meet timing criteria and EBR records are present. | verification-requirements | Verification Requirements |  | Test | 71 |  | SUB-REQ-061 is a SIL-tagged safety requirement covering the MES watchdog timer and operator E-STOP — both are safety-critical functions for the Emergency Stop operating mode. IEC 61511 (Functional Safety — Safety Instrumented Systems for the Process Industry Sector) requires Test verification for SIL-rated functions; Analysis or Inspection alone cannot demonstrate that the actual hardware/software combination meets the 30-second watchdog timeout and 10-second E-STOP response. The HVAC failsafe confirmation is critical because HVAC exhaust mode is the H-001 containment breach safe state. | session-565, validation, mes, watchdog, estop, sil-2, safety-critical, idempotency:session565-ver-subreq061-mes-watchdog
VER-REQ-102 | The verification activity for SUB-REQ-062 SHALL conduct a commissioning inspection of all environmental monitoring sensor installations: (a) verify differential pressure transmitters are present at each of the three controlled cleanroom boundaries by physical walkthrough against installation drawing; (b) confirm temperature and humidity sensor mounting heights are within 0.8–1.2 m above finished floor level using calibrated measuring tape at each classified bay; (c) verify 316L stainless steel construction for all sensor housings by material certification; (d) confirm ISO 8 installation certificate signed by QA for each bay. Pass criterion: all four checks confirmed at all locations. | verification-requirements | Verification Requirements |  | Inspection | 86 |  | SUB-REQ-062 governs physical sensor placement and material certification — Inspection is the correct method as the requirement is verified by physical presence, position measurement, and certificate review, not by dynamic testing. The commissioning inspection is conducted against installation drawings and GMP qualification records and forms part of the Installation Qualification (IQ) package per ISPE Baseline Guide Volume 5 (Commissioning and Qualification). | session-565, validation, environmental-control, sensor-installation, idempotency:session565-ver-subreq062-sensor-install
VER-REQ-103 | The verification activity for SYS-REQ-026 SHALL install reference traceable standards at three cleanroom monitoring points, confirm each differential pressure transmitter reads within ±1 Pa of the reference standard at 0, 50, and 100 Pa calibration points; each temperature transmitter reads within ±0.3°C at 15°C, 22°C, and 30°C; each RH transmitter reads within ±2% RH at 30%, 50%, and 70% RH. Pass criterion: all calibration points within stated tolerances for all installed sensors, confirmed against ISO 17025-accredited calibration records. | verification-requirements | Verification Requirements |  | Test | 86 |  | SYS-REQ-026 specifies sensor accuracy requirements (±1 Pa, ±0.3°C, ±2% RH) and calibration intervals. These tolerances must be demonstrated by calibration test against traceable reference standards — instrument specification alone does not demonstrate field accuracy after installation. ISO 17025-accredited calibration records provide the regulatory evidence required for GMP instrument qualification. | session-566, validation, cleanroom, environmental, physical-embodiment, idempotency:ses566-ver-sys026-cleanroom-sensors
VER-REQ-104 | The verification activity for SYS-REQ-027 SHALL confirm: (a) with PLC in RUN mode, pressing the manual override pushbutton at each equipment panel de-energises the target actuator within 250 ms (measured via oscilloscope on the actuator power circuit); (b) initiating an Emergency Stop via a hardwired safety relay input (bypassing software) de-energises all drives within 250 ms; (c) the override actions do not require any software acknowledgement and are effective regardless of recipe or interlock state. Pass criterion: all actuators de-energised within 250 ms on every test, 100% success rate across 10 consecutive tests per actuator type. | verification-requirements | Verification Requirements |  | Test | 86 |  | SYS-REQ-027 specifies hardware-enforced overrides and 250ms E-stop response. The 250ms timing must be measured with an oscilloscope on the power circuit — software timing logs are insufficient because software failure is the scenario being mitigated. Testing with PLC in RUN mode confirms override works under normal software conditions; hardware bypass test (direct relay input) confirms override is independent of software state. EN ISO 13849-1 requires demonstrated performance level for safety-related control functions. | session-566, validation, process-control-system, safety-override, sil-2, idempotency:ses566-ver-sys027-pcs-override
VER-REQ-105 | The verification activity for SYS-REQ-023 SHALL: (a) log in as a qualified Production Supervisor in the MES test environment; (b) trigger a PAT-induced automated batch diversion; (c) invoke the operator override function and confirm the system requests 21 CFR Part 11 electronic signature before accepting the override; (d) confirm the diversion is suspended and the override timer starts; (e) confirm the system automatically restores automated diversion control after 60 minutes without operator action; (f) confirm the audit trail records operator identity, override reason, start time, and duration. Pass criteria: 21 CFR Part 11 e-sig enforced on all override invocations; auto-restore within 60 minutes (±30 seconds); all 5 audit trail fields populated. | verification-requirements | Verification Requirements |  | Test |  |  | SYS-REQ-023 (operator override capability, 21 CFR Part 11, 60-minute auto-restore) was identified as having no VER trace in the validation session. The override function is safety-relevant because suspension of automated diversion without audit trail creates H-004 (OOS product release) risk. Test verification is required to confirm: (1) electronic signature cannot be bypassed, (2) auto-restore timeout functions correctly, and (3) audit trail is complete per 21 CFR Part 11 requirements. | session-567, validation, override, normal-production, 21-cfr-part-11, sys-023, idempotency:session567-ver-sys023-operator-override
VER-REQ-106 | The verification activity for SYS-REQ-022 SHALL conduct a commissioning inspection of the manufacturing facility against the approved GMP facility layout drawing: (a) confirm presence of at least four classified cleanrooms (weigh booth, granulation/compression, coating/packaging, and materials corridor) by physical walkthrough; (b) confirm ISO 7/Grade C classification certificate for the weigh booth and ISO 8/Grade D classification for remaining production bays by review of environmental monitoring qualification certificates; (c) confirm positive pressure cascade from cleanest to less-clean zones via magnehelic gauge readings at each boundary; (d) confirm dedicated access airlocks at each classified zone boundary. Pass criterion: all four zone certificates present, signed by QA; pressure cascade confirmed in the correct direction at all boundaries. | verification-requirements | Verification Requirements |  | Inspection |  |  | SYS-REQ-022 is a facility layout inspection requirement (ISO 7/Grade C cleanrooms). Inspection is the appropriate verification method since compliance is demonstrated by facility qualification certificates and physical walkthrough, not by instrument test. EU GMP Annex 1 requires documented environmental classification for each cleanroom zone. | session-567, validation, facility, cleanroom, sys-022, idempotency:session567-ver-sys022-facility-layout
VER-REQ-107 | The verification activity for SYS-REQ-025 SHALL inspect the installed environmental monitoring sensor positions in each classified bay: (a) measure mounting height of temperature and humidity sensors at each of the three classified bays with a calibrated measuring tape and confirm all sensors are within 0.8 to 1.2 m above finished floor level; (b) confirm differential pressure transmitters are positioned at each of three controlled cleanroom boundaries; (c) confirm all sensor cables route to the EMS rack and that the EMS controller is within the classified area. Pass criterion: all sensor positions within specified height range; differential pressure taps at all three boundaries; EMS rack location confirmed. | verification-requirements | Verification Requirements |  | Inspection |  |  | SYS-REQ-025 specifies physical sensor mounting positions (0.8-1.2m height, three DP boundaries). Inspection is appropriate as sensor placement is verified by physical measurement during commissioning. No VER trace existed prior to this session. | session-567, validation, sensors, physical-embodiment, sys-025, idempotency:session567-ver-sys025-sensor-placement
VER-REQ-108 | The verification activity for SYS-REQ-028 SHALL perform a physical commissioning inspection of the GMP equipment rack housing the EMS controller, PCS I/O modules, and 4-20mA signal conditioning hardware: (a) confirm the enclosure IP rating is IP54 or better by inspection of the manufacturer certificate; (b) confirm stainless steel construction by visual inspection and material certificate; (c) confirm the rack is installed within the manufacturing line classified area by physical location check against the approved facility layout drawing; (d) confirm connection to the clean power UPS supply by following the UPS output cable to the rack power inlet and verifying the UPS label matches SYS-REQ-007 specification; (e) confirm at least three 4-20mA input channels are wired to differential pressure transmitters at the three cleanroom boundaries. Pass criterion: all five checks confirmed and documented in the commissioning inspection record. | verification-requirements | Verification Requirements |  | Inspection |  |  | SYS-REQ-028 specifies the physical attributes of the environmental monitoring rack (IP54, stainless steel, location in classified area, UPS connection, 4-20mA channels). Inspection is the appropriate verification method: physical attributes are confirmed by inspection and review of material certificates rather than by instrument testing. The inspection record provides the documentary evidence required for GMP facility qualification. | session-568, validation, normal-production, physical-embodiment, mes, sys-028, idempotency:session568-ver-sys028-rack-inspection
VER-REQ-115 | Verify SYS-REQ-030: Inspect PCS network architecture documentation to confirm firewall or unidirectional gateway separates PCS from enterprise IT network. Review network topology diagram and firewall ruleset. Verify IEC 62443-3-3 Security Level 2 compliance assessment is documented. Test access control by attempting HMI login with invalid credentials and verify lockout occurs. Review user access matrix to confirm individual authentication is in place. | verification-requirements | Verification Requirements |  | Inspection |  |  | Network isolation and access control for safety-critical OT systems cannot be fully tested at the system level without risk of disrupting live production. Inspection of documented architecture and security assessment, combined with targeted authentication testing, provides the required verification for a safety-functional cybersecurity requirement. | session-549, qc, cybersecurity, pcs, verification, idempotency:ver-sys-req-030-pcs-cyber-session-549

## Trace Links
Source Ref | Target Ref | Link Type | Description | Rationale | Created
VER-REQ-115 | SYS-REQ-030 | verifies | VER-REQ-115 verifies SYS-REQ-030 PCS cybersecurity | VER-REQ-115 directly verifies the network isolation and access control requirements of SYS-REQ-030 through architecture inspection and targeted access control testing. | 2026-03-26T00:11:10.044Z
STK-REQ-006 | SYS-REQ-030 | derives | STK-REQ-006 GMP compliance derives SYS-REQ-030 PCS cybersecurity | STK-REQ-006 mandates EU GMP compliance including EU GMP Annex 11 (Computerised Systems), which requires access controls and audit trails on GxP software. SYS-REQ-030 implements the network-level controls that protect Annex 11 compliance for the PCS. | 2026-03-26T00:11:09.369Z
uht-bot:se-pharma-manufacturing:VER-110 | uht-bot:se-pharma-manufacturing:IFC-021 | verifies | IFC-021 EMS-MES OPC UA → VER-110 integration latency test | VER-110 directly tests the 10-second latency and audit trail requirements of IFC-021 under production-representative load conditions. | 2026-03-26T00:03:18.791Z
uht-bot:se-pharma-manufacturing:VER-111 | uht-bot:se-pharma-manufacturing:IFC-022 | verifies | IFC-022 hardwired safety bus → VER-111 fail-safe disconnection test | VER-111 physically tests the fail-safe open-circuit behaviour and 100ms latency of the hardwired SIL-2 interface, which is the primary architectural requirement of IFC-022. | 2026-03-26T00:03:18.374Z
uht-bot:se-pharma-manufacturing:VER-109 | SUB-REQ-065 | verifies | SUB-REQ-065 safe state transition → VER-109 30-second response test | VER-109 verifies the specific timing and sequence of the SIL-2 safe state transition defined in SUB-REQ-065 under simulated fault conditions. | 2026-03-26T00:03:17.983Z
uht-bot:se-pharma-manufacturing:VER-108 | SUB-REQ-063 | verifies | SUB-REQ-063 HVAC cleanroom conditions → VER-108 FAT acceptance test | VER-108 verifies the specific temperature, humidity, and ACH parameters defined in SUB-REQ-063 through a controlled factory acceptance test with six spatial measurement points. | 2026-03-26T00:03:17.583Z
uht-bot:se-pharma-manufacturing:VER-112 | SYS-REQ-013 | verifies | SYS-REQ-013 OEL containment → VER-112 end-to-end safety chain test | VER-112 tests the complete safety chain from OEL breach detection through containment response and EBR recording, directly verifying the system-level commitment in SYS-REQ-013 to maintain worker OEL. | 2026-03-26T00:03:17.175Z
uht-bot:se-pharma-manufacturing:VER-113 | uht-bot:se-pharma-manufacturing:IFC-023 | verifies | IFC-023 dP Controller-HVAC 4-20mA interface → VER PID response test | VER tests the 1-second PID cycle and 5% position tolerance specified in IFC-023 by direct physical measurement at the actuator interface. | 2026-03-26T00:03:16.796Z
uht-bot:se-pharma-manufacturing:VER-114 | SUB-REQ-064 | verifies | SUB-REQ-064 pressure cascade → VER door disturbance test | VER tests the 30-second setpoint recovery criterion in SUB-REQ-064 under worst-case door-open disturbance. | 2026-03-26T00:03:16.368Z
SYS-REQ-006 | SUB-REQ-066 | derives | SYS-REQ-006 60s alarm response → SUB EMS alarm transmission | SUB-REQ-066 allocates the system-level 60-second environmental alarm response in SYS-REQ-006 to the EMS component and adds MES OPC UA transmission to satisfy batch record requirements. | 2026-03-25T23:40:14.642Z
SYS-REQ-004 | SUB-REQ-064 | derives | SYS-REQ-004 negative pressure isolation → SUB pressure cascade | SUB-REQ-064 decomposes SYS-REQ-004 by specifying the measurable HVAC pressure cascade values (-12.5 Pa isolator, +10 Pa between grades) and recovery time that satisfy the system-level isolation mandate. | 2026-03-25T23:40:13.928Z
SYS-REQ-022 | SUB-REQ-068 | derives | SYS-REQ-022 ISO 7 cleanroom requirement → SUB particle count monitoring | SUB-REQ-068 derives from SYS-REQ-022 by specifying the continuous particle monitoring regime required to verify and maintain ISO 7 classification during production, which cannot be inferred from HVAC operation alone. | 2026-03-25T23:39:41.633Z
SYS-REQ-022 | SUB-REQ-063 | derives | SYS-REQ-022 GMP cleanroom specification → SUB HVAC supply air conditions | SUB-REQ-063 decomposes the system-level cleanroom specification in SYS-REQ-022 into specific HVAC supply air parameters (temperature, RH, ACH) that the AHU must deliver to achieve and maintain ISO 7/8 classification. | 2026-03-25T23:39:41.002Z
SYS-REQ-013 | SUB-REQ-065 | derives | SYS-REQ-013 OEL maintenance → SUB containment safe state response | SUB-REQ-065 derives from SYS-REQ-013 by defining the automated containment breach response that enforces the OEL constraint — without an automated 100% exhaust response within 30s, worker OEL cannot be guaranteed for OEB 4/5 releases. | 2026-03-25T23:39:40.298Z
STK-REQ-005 | SYS-REQ-029 | derives | Emergency stop includes dust explosion as triggering event | Emergency stop capability (STK-REQ-005) covers dust explosion scenarios — automatic de-energisation at 25% LEL is a specific instantiation for explosion prevention. | 2026-03-25T23:10:15.201Z
STK-REQ-004 | SYS-REQ-029 | derives | Containment integrity drives dust explosion prevention | Potent compound containment (STK-REQ-004) requires enclosed processing, which concentrates powder creating explosion risk. Dust explosion prevention ensures containment design does not introduce new hazards. | 2026-03-25T23:10:14.523Z
VER-REQ-108 | SYS-REQ-028 | verifies | Rack inspection VER → SYS-REQ-028 physical rack embodiment | REQ-SEPHARMAMANUFACTURING-026 verifies the physical attributes of the GMP equipment rack (IP54, stainless steel, location, UPS, 4-20mA channels) specified in SYS-REQ-028. | 2026-03-25T22:12:39.421Z
VER-REQ-107 | SYS-REQ-025 | verifies | VER-107 → SYS-025 environmental sensor placement inspection | VER-REQ-107 inspects the physical sensor mounting positions specified in SYS-REQ-025 (0.8-1.2m height, three DP boundary positions, EMS rack location). | 2026-03-25T21:49:18.722Z
VER-REQ-106 | SYS-REQ-022 | verifies | VER-106 → SYS-022 facility layout inspection | VER-REQ-106 inspects the four-zone cleanroom facility layout and classification certificates required by SYS-REQ-022. | 2026-03-25T21:49:07.186Z
VER-REQ-105 | SYS-REQ-023 | verifies | VER-105 → SYS-023 operator override test | VER-REQ-105 tests the operator override capability (21 CFR Part 11 e-sig, auto-restore timer, audit trail) which are the three core functional attributes of SYS-REQ-023. | 2026-03-25T21:48:34.296Z
STK-REQ-006 | SYS-REQ-022 | derives | STK GMP compliance derives to SYS GMP facility requirement | SYS-REQ-022 (GMP-compliant facility with Grade B cleanroom antechambers) exists because STK-REQ-006 mandates EU GMP Annex 1 and Annex 15 compliance; the facility classification and HVAC pressure cascade directly implements the Regulatory Authority GMP infrastructure stakeholder need. | 2026-03-25T21:02:58.142Z
STK-REQ-008 | SYS-REQ-010 | derives | STK drug serialisation need derives to SYS DataMatrix barcoding | SYS-REQ-010 (DataMatrix serialisation) exists because STK-REQ-008 requires integration with the drug serialisation system and unique pack identification; barcode application at packaging directly implements the Regulatory Authority and Supply Chain stakeholder serialisation need. | 2026-03-25T21:02:48.151Z
STK-REQ-007 | SYS-REQ-008 | derives | STK product changeover validation derives to SYS cleaning guidance | SYS-REQ-008 (guided validated cleaning procedures) exists because STK-REQ-007 mandates validated changeover achieving cross-contamination below 10 ppm; MES-guided cleaning with in-process verification directly implements the QP and QA Manager changeover validation stakeholder need. | 2026-03-25T21:02:47.450Z
STK-REQ-011 | SYS-REQ-006 | derives | STK cleanroom conditions need derives to SYS cleanroom monitoring | SYS-REQ-006 (continuous cleanroom differential pressure monitoring) exists because STK-REQ-011 mandates Grade C/D cleanroom conditions during normal production; real-time pressure monitoring with alarm is required to maintain and verify the GMP environmental stakeholder need. | 2026-03-25T21:02:46.790Z
STK-REQ-010 | SYS-REQ-007 | derives | STK material traceability need derives to SYS batch genealogy | SYS-REQ-007 (full batch genealogy database) exists because STK-REQ-010 mandates bidirectional traceability of all materials, intermediates, and finished product; the genealogy database directly implements the Regulatory Authority and QA Manager traceability stakeholder need. | 2026-03-25T21:02:46.111Z
STK-REQ-009 | SYS-REQ-009 | derives | STK sensor degradation tolerance derives to SYS degraded-mode IPC | SYS-REQ-009 (automatic switch to manual IPC on sensor-degraded mode) exists because STK-REQ-009 mandates continued production during non-critical faults; the degraded-mode fallback directly implements the Operations Director stakeholder need to avoid unnecessary production shutdowns. | 2026-03-25T21:02:45.398Z
STK-REQ-001 | SYS-REQ-017 | derives | STK OEE 75% target derives to SYS OEE monitoring | SYS-REQ-017 (OEE calculation and display per SEMI E10) exists because STK-REQ-001 mandates minimum 75% OEE; real-time OEE monitoring is required to demonstrate and maintain compliance with the Production Manager and Operations Director efficiency target. | 2026-03-25T21:02:31.562Z
STK-REQ-013 | SYS-REQ-012 | derives | STK pharmacopoeial compliance derives to SYS tablet rejection | SYS-REQ-012 (automated tablet rejection outside weight/hardness tolerance) exists because STK-REQ-013 mandates pharmacopoeial compliance for finished drug product; in-process rejection of out-of-spec tablets directly implements the patient safety stakeholder need. | 2026-03-25T21:02:30.917Z
STK-REQ-003 | SYS-REQ-003 | derives | STK PAT monitoring need derives to SYS PAT data acquisition | SYS-REQ-003 (PAT sensor data acquisition at minimum intervals) exists because STK-REQ-003 mandates continuous real-time PAT monitoring; the sample interval requirements operationalise the QP/QA stakeholder need for uninterrupted CQA surveillance. | 2026-03-25T21:02:30.259Z
STK-REQ-002 | SYS-REQ-002 | derives | STK EBR compliance need derives to SYS EBR generation | SYS-REQ-002 (EBR generation and archival with electronic signatures) exists because STK-REQ-002 requires 21 CFR Part 11 compliant EBRs; the system-level EBR requirement directly implements the regulatory authority and QA Manager stakeholder compliance need. | 2026-03-25T21:02:29.563Z
STK-REQ-012 | SYS-REQ-011 | derives | STK LOTO need derives to SYS electronic LOTO enforcement | SYS-REQ-011 (electronic LOTO verification) exists because STK-REQ-012 mandates documented LOTO procedures with physical isolation verification; MES-enforced electronic lockout directly implements the maintenance safety stakeholder need. | 2026-03-25T21:02:14.629Z
STK-REQ-005 | SYS-REQ-005 | derives | STK emergency stop need derives to SYS emergency stop response | SYS-REQ-005 (emergency stop response within 10 s) exists because STK-REQ-005 mandates controlled full-stop on any emergency condition; the 10-second response time operationalises the operator safety need and underpins H-001/H-007 hazard mitigation. | 2026-03-25T21:02:13.925Z
STK-REQ-004 | SYS-REQ-004 | derives | STK OEL containment derives to SYS negative pressure isolation | SYS-REQ-004 (negative pressure isolation) exists because STK-REQ-004 mandates OEL containment for OEB 3-5 compounds; -50 Pa minimum setpoint directly implements the EHS Officer stakeholder containment integrity need. | 2026-03-25T21:02:13.243Z
VER-REQ-001 | SUB-REQ-003 | verifies | CQA model evaluation timing test | SIL-3 H-004: model latency determines OOS tablet exposure window; test confirms 2-second bound and OOS detection completeness | 2026-03-25T21:01:47.897Z
VER-REQ-002 | SUB-REQ-004 | verifies | Diversion valve actuation time and fail-safe test | SIL-3 H-004: valve timing and spring-return must be tested under all operating conditions to confirm safe-state reachability | 2026-03-25T21:01:47.490Z
VER-REQ-003 | SUB-REQ-005 | verifies | Sensor degradation detection test | SIL-3 H-004: missed sensor degradation means OOS product can pass undetected; test confirms detection within 15-second window | 2026-03-25T21:01:47.083Z
VER-REQ-004 | IFC-REQ-001 | verifies | CQA alarm delivery and soak test | SIL-3 interface: alarm loss or latency beyond 500ms enables OOS tablet release; soak test detects intermittent OPC-UA failures | 2026-03-25T21:01:46.665Z
VER-REQ-005 | IFC-REQ-003 | verifies | Diversion acknowledgment delivery test | SIL-3 interface: acknowledgment confirms MES registration of diversion event; without it PAT cannot distinguish new from duplicate alarms | 2026-03-25T21:01:46.234Z
VER-REQ-006 | SUB-REQ-008 | verifies | 21 CFR Part 11 e-signature enforcement test | SIL-2 H-006: unauthenticated EBR entries are inadmissible under 21 CFR Part 11; 100% rejection must be demonstrated for each critical action | 2026-03-25T21:01:45.871Z
VER-REQ-007 | SUB-REQ-011 | verifies | LOTO restart prevention test | SIL-2 H-007: the test must exercise OPC-UA programmatic restart path as well as HMI path to cover all restart vectors that could bypass LOTO | 2026-03-25T21:01:45.497Z
VER-REQ-008 | SUB-REQ-010 | verifies | SHA-256 hash chain tamper detection test | SIL-2 H-006: direct database manipulation test simulates the primary threat model for 21 CFR Part 11 electronic records | 2026-03-25T21:01:45.104Z
VER-REQ-009 | SYS-REQ-003 | verifies | System-level PAT diversion chain integration test | SYS PAT timing and diversion requirement requires an end-to-end test that exercises the full sensor-to-actuator path under load, not just individual component verification | 2026-03-25T21:01:44.744Z
VER-REQ-010 | SUB-REQ-002 | verifies | Raman spectrometer OQ performance test | Instrument qualification test verifies spectral resolution and acquisition timing against specification | 2026-03-25T21:01:44.343Z
VER-REQ-011 | SUB-REQ-007 | verifies | Laser diffraction OQ particle size accuracy test | Instrument qualification test with NIST-traceable reference standards confirms D50/D90 accuracy and repeatability against specification | 2026-03-25T21:01:43.979Z
VER-REQ-012 | SUB-REQ-015 | verifies | Paper backup fallback demonstration on integrity failure | SIL-2 H-006 safe state demonstration: confirms MES transitions to paper records within required timeframe on EBR integrity failure | 2026-03-25T21:01:43.580Z
VER-REQ-013 | IFC-REQ-006 | verifies | Integration test for G&B-to-PAT NIR interface latency | VER-REQ-013 tests the specific latency and data integrity parameters defined in IFC-REQ-006 under controlled conditions using calibrated reference spectra. | 2026-03-25T21:01:43.199Z
VER-REQ-014 | IFC-REQ-007 | verifies | Integration test for MES-to-G&B recipe delivery and EBR feedback | VER-REQ-014 tests the 2-second setpoint delivery and 10-second EBR feedback interval requirements specified in IFC-REQ-007. | 2026-03-25T21:01:42.842Z
VER-REQ-015 | SUB-REQ-016 | verifies | End-to-end G&B cycle test verifies HSG endpoint detection as first criterion | VER-REQ-015 includes HSG endpoint criterion 1 as the first PASS criterion, providing direct verification coverage for SUB-REQ-016. | 2026-03-25T21:01:42.472Z
VER-REQ-015 | SUB-REQ-017 | verifies | End-to-end G&B cycle test verifies FBD LOD drying endpoint | VER-REQ-015 criterion 2 (FBD LOD within target plus or minus 0.5%) directly verifies the SUB-REQ-017 LOD acceptance requirement. | 2026-03-25T21:01:42.082Z
VER-REQ-016 | IFC-REQ-008 | verifies | Inspection test for G&B-to-Compression sealed IBC handoff | VER-REQ-016 tests the sealed IBC transfer protocol and MES genealogy chain defined in IFC-REQ-008. | 2026-03-25T21:01:41.689Z
VER-REQ-017 | IFC-REQ-002 | verifies | VER-REQ-017 verifies PAT sensor health status publishing via OPC UA | VER-REQ-017 tests the OPC UA publish cycle, field completeness, and sensor state machine transitions defined in IFC-REQ-002 by injecting a controlled NIR degradation and measuring MES receipt latency. | 2026-03-25T21:01:41.297Z
VER-REQ-018 | IFC-REQ-004 | verifies | VER-REQ-018 verifies CQA measurement stream latency and diversion trigger | VER-REQ-018 tests IFC-REQ-004 end-to-end: CQA data streams, MES OPC UA subscription latency (<=2s p99), and diversion command generation on OOS detection. This is the critical-path verification for batch quality control. | 2026-03-25T21:01:40.879Z
VER-REQ-019 | SUB-REQ-009 | verifies | VER-REQ-019 verifies MES tamper-evident audit trail | VER-REQ-019 tests SUB-REQ-009 hash chain integrity and audit trail completeness by attempting direct database modification and verifying the detection mechanism and alert generation within the required 60-second window. | 2026-03-25T21:01:40.493Z
VER-REQ-020 | SUB-REQ-020 | verifies | VER-REQ-020 verifies IBC Blender blend uniformity RSD criterion | VER-REQ-020 tests SUB-REQ-020 blend uniformity acceptance criterion using a 10-sample stratified sampling plan with HPLC analysis per ICH Q2(R1). This is the process validation test that formally confirms the blending unit operation meets the RSD <=5% requirement. | 2026-03-25T21:01:40.095Z
VER-REQ-021 | SUB-REQ-001 | verifies | VER-REQ-021 verifies NIR spectrometer spectral acquisition parameters | VER-REQ-021 validates SUB-REQ-001 spectral range, channel resolution, acquisition latency, and integration time configurability under simulated production conditions. This is the instrument qualification test for the PAT NIR subsystem. | 2026-03-25T21:01:39.728Z
VER-REQ-022 | IFC-REQ-009 | verifies | VER-REQ-022 verifies quantified degraded mode MES-PAT interface | VER-REQ-022 tests the 30-second command delivery, 3-parameter minimum coverage, 5-minute confirmation window, and non-conformance logging defined in IFC-REQ-009. | 2026-03-25T21:01:39.334Z
VER-REQ-023 | SUB-REQ-024 | verifies | VER-REQ-023 verifies quantified PAT sensor-degraded performance floor | VER-REQ-023 tests the 10s suspension window, 2-of-3 channel minimum, 60s prompt window, and safe-state transition on 2-sensor failure defined in SUB-REQ-024. | 2026-03-25T21:01:38.953Z
VER-REQ-023 | SUB-REQ-006 | verifies | PAT channel-degraded CQA suspension verified by induced degradation test | SUB-REQ-006 requires the PAT subsystem to suspend CQA model evaluation on a degraded channel while continuing on the remaining 2 channels. VER-REQ-023 verifies this by inducing degradation on one NIR channel and measuring the suspension latency and multi-channel continuity — directly testing the degraded-state behaviour specified in SUB-REQ-006. | 2026-03-25T21:01:38.558Z
VER-REQ-007 | SUB-REQ-012 | verifies | LOTO event logging verified as part of LOTO registry and restart-prevention test | SUB-REQ-012 requires the MES to log every LOTO event with operator identity and timestamp in the audit trail. VER-REQ-007 applies a maintenance lock and verifies restart prevention — by inspecting the resulting LOTO registry log entries, the test also validates the event recording requirement of SUB-REQ-012. | 2026-03-25T21:01:38.162Z
VER-REQ-016 | SUB-REQ-013 | verifies | MES batch genealogy recording verified by end-of-cycle genealogy record inspection | SUB-REQ-013 requires the MES to record batch genealogy linking each production batch to raw material lot numbers and equipment usage records. VER-REQ-016 completes a G&B cycle and inspects the MES batch genealogy record for IBC mass, blend authorisation code, and lot number — directly confirming the genealogy linkage specified in SUB-REQ-013. | 2026-03-25T21:01:37.777Z
VER-REQ-012 | SUB-REQ-014 | verifies | EBR backup and recovery capability verified as part of data integrity failure simulation | SUB-REQ-014 requires automated EBR database backups at ≤15-minute intervals with offsite mirroring. VER-REQ-012 simulates an EBR data integrity failure and confirms fallback to paper recording — this test exercises the backup and recovery path, confirming that recovery from a verified backup is possible within the operational requirements of SUB-REQ-014. | 2026-03-25T21:01:37.394Z
VER-REQ-015 | SUB-REQ-018 | verifies | FBD temperature control tolerance verified within end-to-end G&B cycle test | SUB-REQ-018 requires the FBD to maintain inlet air temperature within ±2°C of MES recipe setpoint throughout drying. VER-REQ-015 validates a complete G&B cycle with confirmation of endpoint achievement — the temperature control performance of the FBD is exercised and measured as part of this end-to-end cycle, verifying the tolerance band of SUB-REQ-018. | 2026-03-25T21:01:36.990Z
VER-REQ-015 | SUB-REQ-019 | verifies | Granule sizing D90 limit verified within end-to-end G&B cycle IPC measurements | SUB-REQ-019 requires the Granule Sizing Mill to reduce dried granule agglomerates to D90 ≤ 1 mm after sizing. VER-REQ-015 validates a complete G&B cycle with endpoint confirmation — granule PSD is measured as part of the cycle IPC, verifying the sizing performance requirement of SUB-REQ-019. | 2026-03-25T21:01:36.599Z
VER-REQ-016 | SUB-REQ-021 | verifies | G&B step-mass recording verified by post-cycle batch genealogy record inspection | SUB-REQ-021 requires the G&B subsystem to record the mass of each material charge and transfer at every process step. VER-REQ-016 inspects the MES batch genealogy record after a complete G&B cycle and confirms presence of IBC mass, blend authorisation code, and lot number — the mass recording chain of SUB-REQ-021 is directly inspected in this verification. | 2026-03-25T21:01:36.213Z
VER-REQ-022 | SUB-REQ-022 | verifies | PAT NIR blend-endpoint unavailability fallback verified by degraded-mode transition test | SUB-REQ-022 requires the G&B subsystem to fall back to a validated fixed-time blending protocol when PAT NIR blend-endpoint monitoring is unavailable. VER-REQ-022 triggers a PAT degraded-mode transition and measures MES command receipt — this test exercises the NIR unavailability scenario that triggers the fallback specified in SUB-REQ-022. | 2026-03-25T21:01:35.823Z
VER-REQ-015 | SUB-REQ-023 | verifies | G&B containment under OEB 3 potency conditions verified within end-to-end cycle test | SUB-REQ-023 requires the G&B subsystem to maintain negative-pressure containment (OEB 3, OEL <10 µg/m³) throughout processing of potent compounds. VER-REQ-015 completes a full G&B cycle and includes containment inspection — negative-pressure maintenance during granulation and blending operations must be confirmed as part of this cycle for potent compound products. | 2026-03-25T21:01:35.423Z
VER-REQ-005 | IFC-REQ-005 | verifies | MES diversion command transmission latency verified by CQA alarm-to-acknowledgment timing test | IFC-REQ-005 specifies that when the MES transitions to diversion mode it must transmit the diversion command to the PAT DAC Workstation within a defined latency. VER-REQ-005 measures the time from CQA alarm receipt at MES to diversion acknowledgment transmission — this is the return path of the diversion command that IFC-REQ-005 specifies. | 2026-03-25T21:01:35.016Z
VER-REQ-024 | SUB-REQ-027 | verifies | Guard door LOTO interlock test verifies SUB-REQ-027 | The 10-trial demonstration with 500 ms stop time measurement and LOTO clearance verification directly tests both quantitative acceptance criteria in SUB-REQ-027 — stop time and restart prevention. | 2026-03-25T21:01:34.643Z
VER-REQ-025 | SUB-REQ-028 | verifies | Containment pressure test verifies SUB-REQ-028 | The test verifies both steady-state pressure band and alarm/hold response time — the two measurable acceptance criteria in SUB-REQ-028. | 2026-03-25T21:01:34.247Z
VER-REQ-026 | IFC-REQ-010 | verifies | OPC-UA data stream test verifies IFC-REQ-010 | The 30-minute production run test checks message rate, timestamp accuracy, and channel completeness — all three acceptance criteria in IFC-REQ-010. | 2026-03-25T21:01:33.830Z
VER-REQ-027 | IFC-REQ-011 | verifies | MES EBR write test verifies IFC-REQ-011 | The injected-event test verifies event capture completeness and 10-second write latency — the two acceptance criteria in IFC-REQ-011. | 2026-03-25T21:01:33.429Z
VER-REQ-104 | SYS-REQ-027 | verifies | Hardware override test verifies PCS manual override and E-stop timing | SYS-REQ-027 requires hardware-enforced overrides independent of software state. Oscilloscope test of actuator power circuit directly verifies 250ms response without depending on software timing. | 2026-03-25T20:51:42.112Z
VER-REQ-103 | SYS-REQ-026 | verifies | Calibration test verifies cleanroom sensor accuracy | SYS-REQ-026 specifies ±1 Pa, ±0.3°C, ±2% RH accuracy tolerances. Calibration test against ISO 17025 traceable standards directly verifies these tolerances are met in the installed configuration. | 2026-03-25T20:51:41.435Z
VER-REQ-094 | SYS-REQ-002 | verifies | EBR lifecycle test verifies system EBR integrity requirement | SYS-REQ-002 SIL-2 H-006 data integrity — VER-REQ-094 provides Test verification of EBR lifecycle, electronic signatures, 15-min backup interval, and cryptographic tamper detection. | 2026-03-25T20:38:58.801Z
uht-bot:se-pharma-manufacturing:ARC-REQ-009 | ARC-REQ-007 | derives | Duplicate PCS power requirement (condensed) linked to canonical version | ARC-REQ-009 is a condensed duplicate of ARC-REQ-007 (tagged duplicate-of-ARC-REQ-007); linked here to ensure orphan resolution before QC deletion. | 2026-03-25T20:15:55.128Z
uht-bot:se-pharma-manufacturing:ARC-REQ-008 | ARC-REQ-007 | derives | Duplicate PCS power requirement linked to canonical version | ARC-REQ-008 is a near-duplicate of ARC-REQ-007 (tagged duplicate-of-ARC-REQ-007); linked here to ensure orphan resolution before QC deletion. | 2026-03-25T20:15:54.457Z
ARC-REQ-003 | ARC-REQ-007 | derives | Granulation equipment train architecture drives PCS power supply specification | ARC-REQ-003 defines the granulation equipment train (HSG, FBD, bin blender); ARC-REQ-007 specifies the 24 VDC PCS power architecture that supplies all three units in that train, derived from the need to power the process train continuously with UPS backup for safe shutdown. | 2026-03-25T20:15:07.333Z
ARC-REQ-002 | ARC-REQ-006 | derives | MES module decomposition drives software validation category decision | ARC-REQ-002 defines the MES as five functional modules requiring pharmaceutical-grade validation; ARC-REQ-006 captures the validation strategy (GAMP 5 Category 4, FDA 21 CFR Part 11, EU GMP Annex 11) for the overall MES. | 2026-03-25T20:14:57.051Z
ARC-REQ-002 | ARC-REQ-005 | derives | MES functional decomposition drives hardware deployment architecture | ARC-REQ-002 defines the MES functional module decomposition; ARC-REQ-005 is the deployment architecture for the MES modules — server pair specification derives from the requirement to host all five MES modules with 21 CFR Part 11 compliance and 20-user concurrent access. | 2026-03-25T20:14:56.258Z
VER-REQ-102 | SUB-REQ-062 | verifies | Inspection protocol for environmental sensor installation commissioning | VER-REQ-102 provides the commissioning Inspection protocol confirming sensor placement, mounting height, material certification, and GMP qualification records required by SUB-REQ-062. | 2026-03-25T20:11:44.359Z
SYS-REQ-022 | SUB-REQ-062 | derives | Cleanroom facility requirement implemented by environmental sensor installation in each bay | SYS-REQ-022 defines the four classified cleanroom bays of the facility; SUB-REQ-062 specifies the environmental sensor installation at each bay boundary, implementing the environmental monitoring infrastructure required to maintain the classified zones defined in SYS-REQ-022. | 2026-03-25T20:11:20.175Z
SYS-REQ-025 | SUB-REQ-062 | derives | System-level sensor installation requirement decomposed to environmental control subsystem | SYS-REQ-025 specifies sensor placement and material standards at system level; SUB-REQ-062 implements these requirements at the Containment and Environmental Control Subsystem level with specific installation locations and height criteria per EU GMP Annex 1. | 2026-03-25T20:11:19.516Z
SYS-REQ-023 | SUB-REQ-061 | derives | System override requirement derived to MES E-STOP workstation override | SYS-REQ-023 requires operator override with production supervisor role credentials; SUB-REQ-061 implements the complementary E-STOP physical override capability at operator workstations — both together constitute the full operator override function for automated production controls. | 2026-03-25T20:10:41.491Z
SYS-REQ-023 | SUB-REQ-058 | derives | System override capability derived to PAT subsystem CQA override implementation | SYS-REQ-023 specifies the system-level operator override capability with electronic signature and 60-minute maximum duration; SUB-REQ-058 implements this override function within the PAT subsystem for CQA-based batch diversion. | 2026-03-25T20:10:40.848Z
SYS-REQ-022 | SUB-REQ-059 | derives | Facility installation requirement decomposed to granulation bay sub-specification | SYS-REQ-022 specifies the four classified cleanroom bays; SUB-REQ-059 implements this at the granulation and blending bay level with specific ISO 8 / Grade D classification and 316L material of construction. | 2026-03-25T20:10:30.016Z
VER-REQ-101 | SUB-REQ-061 | verifies | Test verification of MES watchdog timer and E-STOP safety functions | VER-REQ-101 provides the Test protocol exercising both the MES watchdog timer safe-state transition and the E-STOP response time specified in SUB-REQ-061. | 2026-03-25T20:10:22.519Z
VER-REQ-100 | SUB-REQ-060 | verifies | Test verification of PCS power supply and UPS performance | VER-REQ-100 provides the Test protocol measuring power load, UPS autonomy, alarm response time, and voltage regulation specified in SUB-REQ-060. | 2026-03-25T20:10:21.781Z
VER-REQ-099 | SUB-REQ-059 | verifies | Inspection verification of granulation bay installation standards | VER-REQ-099 provides the Inspection protocol confirming SUB-REQ-059's ISO 8 cleanroom, 316L steel, and OEB 4 transfer connection installation requirements. | 2026-03-25T20:10:12.339Z
VER-REQ-097 | SYS-REQ-012 | verifies | System-level IPC automated rejection verification | VER-REQ-097 injects 10 OOS tablets via compression roll adjustment and confirms automated IPC rejection; pass demonstrates SYS-REQ-012 compliance for automated in-process rejection within ±5% weight tolerance. | 2026-03-25T19:33:23.314Z
VER-REQ-096 | SYS-REQ-010 | verifies | System-level packaging serialisation and aggregation verification | VER-REQ-096 runs packaging of 500 saleable units and confirms 100% serialisation with aggregation; pass demonstrates SYS-REQ-010 compliance for EU FMD 2D DataMatrix and unique serial number assignment. | 2026-03-25T19:33:22.637Z
VER-REQ-095 | SYS-REQ-009 | verifies | System-level PAT degraded-mode transition and manual sampling frequency verification | VER-REQ-095 induces PAT sensor-degraded mode during a running production simulation and measures transition latency and sampling frequency; pass demonstrates SYS-REQ-009 compliance for degraded mode switch within performance bounds. | 2026-03-25T19:33:21.992Z
VER-REQ-094 | SYS-REQ-002 | verifies | System-level EBR lifecycle and 21 CFR Part 11 compliance verification | VER-REQ-094 executes a complete batch lifecycle in MES test environment with e-signature and audit trail; pass demonstrates SYS-REQ-002 compliance for 21 CFR Part 11 EBR integrity at SIL-2. | 2026-03-25T19:33:21.374Z
VER-REQ-093 | SYS-REQ-001 | verifies | System-level throughput and OEE verification via continuous production run | VER-REQ-093 runs a 12-hour simulated production campaign at nominal recipe; pass demonstrates SYS-REQ-001 compliance for throughput and OEE targets across the full production sequence. | 2026-03-25T19:33:20.700Z
VER-REQ-092 | SYS-REQ-011 | verifies | System-level LOTO electronic lockout enforcement verification | VER-REQ-092 tests LOTO enforcement via three separate equipment isolations; pass demonstrates SYS-REQ-011 compliance for preventing equipment restart under active lockout at SIL-2. | 2026-03-25T19:33:04.405Z
VER-REQ-091 | SYS-REQ-004 | verifies | System-level containment negative pressure and HVAC verification | VER-REQ-091 tests negative pressure containment and HVAC exhaust response; pass demonstrates SYS-REQ-004 compliance for OEB4/5 containment at SIL-2. | 2026-03-25T19:33:03.719Z
VER-REQ-090 | SYS-REQ-003 | verifies | System-level PAT CQA model accuracy verification | VER-REQ-090 injects 50 pre-characterised CQA spectra to test PAT model accuracy; pass demonstrates SYS-REQ-003 compliance for OOS detection and batch diversion at SIL-3. | 2026-03-25T19:33:03.087Z
VER-REQ-098 | SUB-REQ-058 | verifies | PAT autonomy override mechanism Test (IEC 61508 Functional Autonomy Safety Constraint) | SUB-REQ-058 addresses IEC 61508 Part 3 requirements for bounded and auditable override of functionally autonomous safety functions | 2026-03-25T19:17:22.813Z
VER-REQ-089 | SYS-REQ-007 | verifies | End-to-end batch genealogy verification (SYS-REQ-007) | 21 CFR Part 11 recall capability requires full material lineage traceability from dispensed raw materials to individual finished packs | 2026-03-25T18:41:15.566Z
VER-REQ-088 | SYS-REQ-017 | verifies | OEE dashboard update latency confirmation | OEE dashboard must reflect actual equipment state within one minute to support real-time production management decisions; latency check is separate from SYS-REQ-017 accuracy check | 2026-03-25T18:40:46.576Z
VER-REQ-087 | SYS-REQ-021 | verifies | Shift handover supervisor capability and pending action transfer | Incomplete shift handover is a GMP risk for batch continuity; MES handover feature ensures outgoing supervisor formalises all open actions before relinquishing batch record ownership | 2026-03-25T18:40:45.895Z
VER-REQ-083 | SUB-REQ-056 | verifies | MES batch review package and QA sign-off workflow | Complete batch review package generation is the precondition for Qualified Person certification; verification confirms all mandatory EBR sections populate correctly and QA workflow routes to correct approvers | 2026-03-25T18:40:45.151Z
VER-REQ-082 | SUB-REQ-055 | verifies | LIMS sample request receipt within MES 30-minute SLA | LIMS integration latency determines how quickly QC analyst receives IPC samples; 30-minute SLA bounds the impact on batch release timeline for time-critical stability samples | 2026-03-25T18:40:44.466Z
VER-REQ-081 | SUB-REQ-054 | verifies | Packaging vision inspection 100 percent coverage | Vision inspection is the final patient safety check before unit-level serialisation; 500-pack test at line speed with seeded defects confirms detection rate at the specified threshold | 2026-03-25T18:40:43.761Z
VER-REQ-079 | SUB-REQ-052 | verifies | Tablet Compression metal detection per-tablet check | Per-tablet metal detection is the patient safety barrier for foreign metal from punch tip fracture; test with known metal insert at minimum detectable size confirms instrument sensitivity | 2026-03-25T18:40:43.096Z
VER-REQ-076 | SUB-REQ-049 | verifies | CEC continuous air monitoring frequency and data logging | Continuous monitoring at the defined sampling interval is necessary to detect transient concentration spikes; logging confirms data integrity and provides evidence trail for operator exposure records | 2026-03-25T18:40:42.383Z
VER-REQ-074 | SUB-REQ-047 | verifies | Degraded Production mode batch quarantine and QA release gate | Degraded mode batches carry increased quality risk from reduced PAT confidence; automated quarantine with QA Manager sign-off gate ensures every degraded-mode batch receives human disposition review | 2026-03-25T18:40:41.615Z
VER-REQ-073 | SUB-REQ-044 | verifies | Startup mode entry criteria and production mode gate | Startup qualification gate prevents production from starting on unqualified equipment; MES must enforce all IQ/OQ/PQ sign-off records before releasing the batch record for initiation | 2026-03-25T18:40:40.905Z
VER-REQ-072 | SUB-REQ-043 | verifies | MES server hardware rack and environmental controls | 21 CFR Part 11 requires EBR to be maintained on secure, controlled hardware; physical inspection confirms server room access controls, temperature and humidity monitoring are in place | 2026-03-25T18:40:40.259Z
VER-REQ-070 | SUB-REQ-041 | verifies | Film Coating Subsystem 400V power supply | Film coating pan must maintain inlet air temperature and drum rotation throughout coating cycle; power supply specification ensures process cannot be interrupted by transient electrical events | 2026-03-25T18:40:39.566Z
VER-REQ-069 | SUB-REQ-040 | verifies | Granulation and Blending Subsystem 400V power supply | Power supply integrity for granulation equipment ensures process continuity during granulation critical steps where power interruption would compromise batch homogeneity | 2026-03-25T18:40:38.887Z
VER-REQ-068 | SUB-REQ-039 | verifies | Tablet Compression Subsystem EPO power interruption response | Tablet press must reach zero energy state within EPO response time to protect operators during mechanical jam events; power measurement confirms energy state for LOTO authorisation | 2026-03-25T18:40:38.168Z
VER-REQ-060 | SYS-REQ-017 | verifies | OEE tracking per SEMI E10 equipment availability standard | OEE is the primary production performance KPI reported to site management; 24-hour simulated run validates classification of planned stops, unplanned downtime, and quality losses | 2026-03-25T18:40:37.475Z
VER-REQ-058 | SYS-REQ-015 | verifies | EU FMD serialisation and unit-level 2D code generation | EU Delegated Regulation 2016/161 mandates unique identifier on every pack; 1000-pack test exercises the serialisation server at production throughput and confirms aggregation reporting | 2026-03-25T18:40:36.794Z
VER-REQ-057 | SYS-REQ-014 | verifies | ICH Q8/Q11 process validation data recording | ICH Q8 process validation requires complete parametric data across the campaign; system-level verification confirms all CPPs are captured and available for Stage 2 validation reports | 2026-03-25T18:40:36.101Z
VER-REQ-055 | SUB-REQ-026 | verifies | Tablet IPC system sampling rate at nominal press speed | IPC sampling every 30th tablet at 60 RPM defines the statistical basis for in-process control charts; test at nominal speed ensures the sampler mechanism meets the specified throughput | 2026-03-25T18:40:35.450Z
VER-REQ-049 | SUB-REQ-013 | verifies | MES batch genealogy and material lineage tracking | Batch genealogy is a GMP requirement for product recall capability; three-batch simulation exercises IBC and component serial number linkage across full upstream-to-downstream chain | 2026-03-25T18:40:34.772Z
VER-REQ-048 | SUB-REQ-006 | verifies | PAT subsystem degraded-mode NIR channel failure alert | PAT must detect individual channel failures to avoid running CQA model on corrupted spectral data; channel disable test exercises the sensor health monitor without requiring actual instrument degradation | 2026-03-25T18:40:34.027Z
VER-REQ-085 | SYS-REQ-019 | verifies | Automatic deviation record on CPP exceedance (SIL-2) | SIL-2: CPP exceedances without automatic deviation records create undetected product risk; automatic generation ensures QA investigation is triggered in all cases | 2026-03-25T18:39:50.435Z
VER-REQ-080 | SUB-REQ-053 | verifies | Dust explosion inerting and LEL monitoring (SIL-2 H-003) | SIL-2 H-003: dust explosion in granulation equipment is a rare but catastrophic event; inerting trigger at 25% LEL provides a safety margin before the 40% LEL equipment shutdown point | 2026-03-25T18:39:49.792Z
VER-REQ-075 | SUB-REQ-048 | verifies | CEC airborne API concentration breach auto-response (SIL-2 H-001) | SIL-2 H-001: automated response to containment breach is faster than manual intervention; 500ms actuation is required to close valves before API disperses beyond the room | 2026-03-25T18:39:49.101Z
VER-REQ-071 | SUB-REQ-042 | verifies | CEC subsystem UPS power supply (SIL-2 H-001) | SIL-2 H-001: loss of containment HVAC during mains failure would allow airborne API to migrate; UPS bridges the gap until generator assumes load | 2026-03-25T18:39:48.429Z
VER-REQ-066 | SUB-REQ-046 | verifies | Maintenance LOTO MES display enforcement (SIL-2 H-007) | SIL-2 H-007: LOTO display in MES is the administrative control corroborating physical lock; dual confirmation prevents restart while maintenance technician is inside | 2026-03-25T18:39:47.745Z
VER-REQ-065 | SUB-REQ-045 | verifies | Emergency Stop mode exit criteria (SIL-2 H-001) | SIL-2 H-001: post-breach recovery must not proceed until root cause is confirmed corrected; sign-off gate prevents premature restart | 2026-03-25T18:39:47.067Z
VER-REQ-064 | SUB-REQ-038 | verifies | MES watchdog timer EBR processing (SIL-2 H-006) | SIL-2 H-006: MES watchdog is the automated control that detects EBR write failures before a batch record becomes irrecoverable | 2026-03-25T18:39:46.427Z
VER-REQ-059 | SYS-REQ-016 | verifies | EN ISO 13849-1 machine safety PLd/PLe (SIL-2 H-007) | SIL-2 H-007: Performance Level determination is the engineering evidence for mechanical entrapment risk reduction; PLd required for rotating equipment guarding | 2026-03-25T18:39:45.743Z
VER-REQ-056 | SYS-REQ-013 | verifies | OEL containment system requirement (SIL-2 H-001) | SIL-2 H-001: system-level OEL compliance requirement covers all manufacturing areas; verification evidence required for COSHH assessment and operator health monitoring programme | 2026-03-25T18:39:45.070Z
VER-REQ-054 | SUB-REQ-023 | verifies | OEB-3 containment during G+B operations (SIL-2 H-001) | SIL-2 H-001: potent compound exposure during granulation is the highest-frequency containment risk | 2026-03-25T18:39:44.337Z
VER-REQ-053 | SUB-REQ-021 | verifies | G+B mass balance recording (SIL-2 data integrity) | SIL-2: mass balance gaps in granulation records are 21 CFR Part 11 data integrity findings and prevent batch release | 2026-03-25T18:39:43.670Z
VER-REQ-052 | SUB-REQ-019 | verifies | Granule sizing mill PSD requirement (SIL-2) | SIL-2: PSD outside specification directly affects dissolution rate and content uniformity in finished tablets | 2026-03-25T18:39:42.973Z
VER-REQ-051 | SUB-REQ-018 | verifies | FBD inlet air temperature control (SIL-2) | SIL-2: temperature deviation degrades granule quality uniformity leading to content uniformity failures downstream | 2026-03-25T18:39:42.257Z
VER-REQ-050 | SUB-REQ-017 | verifies | FBD LOD drying target (SIL-2 product quality) | SIL-2: insufficient drying leaves moisture above specification leading to tablet physical instability and potential caking in packaging | 2026-03-25T18:39:41.524Z
VER-REQ-086 | SYS-REQ-020 | verifies | VER-REQ-086 verifies the cleaning status registry system requirement (SIL-3 H-002) | SIL-3 H-002: equipment released without confirmed clean status risks cytotoxic carry-over; MES registry gate is the system-level cross-contamination prevention control | 2026-03-25T18:39:14.141Z
VER-REQ-084 | SUB-REQ-057 | verifies | VER-REQ-084 verifies PAT audit log 30-day rolling archive integrity requirement (SIL-3 H-004) | SIL-3 H-004: PAT audit trail is required for FDA data integrity inspection and reconstruction of any OOS batch decision; 30-day archive covers a complete commercial campaign | 2026-03-25T18:39:13.465Z
VER-REQ-078 | SUB-REQ-051 | verifies | VER-REQ-078 verifies two-person independent verification for API dispensing (SIL-3 H-002) | SIL-3 H-002: incorrect API dispensing leads to wrong-strength or wrong-compound product; two-person check is the administrative control corroborated by MES enforcement | 2026-03-25T18:39:12.763Z
VER-REQ-077 | SUB-REQ-050 | verifies | VER-REQ-077 verifies MES cleaning validation failure quarantine enforcement (SIL-3 H-002) | SIL-3 H-002: a failed swab result must immediately prevent the next batch from starting; MES quarantine enforcement is the automated barrier against cross-contamination | 2026-03-25T18:39:12.069Z
VER-REQ-067 | SUB-REQ-047 | verifies | VER-REQ-067 verifies the Degraded Production mode real-time release block (SIL-3 H-004) | SIL-3 H-004: in degraded mode PAT confidence is reduced; blocking RTRT forces HPLC confirmation before release, preventing OOS product reaching patients | 2026-03-25T18:39:11.364Z
VER-REQ-063 | SUB-REQ-037 | verifies | VER-REQ-063 verifies the PAT manual CQA override access control requirement (SIL-3) | SIL-3 H-004: override interface bypasses automated diversion; QC Analyst role restriction is the barrier preventing unauthorised override that would allow OOS product through | 2026-03-25T18:39:10.679Z
VER-REQ-062 | SUB-REQ-036 | verifies | VER-REQ-062 verifies the PAT subsystem dedicated UPS power supply requirement (SIL-3 H-004) | SIL-3 H-004: mains failure during PAT monitoring must not cause undetected OOS tablets; dedicated UPS ensures PAT continues or fails safe to diversion | 2026-03-25T18:39:09.976Z
VER-REQ-061 | SYS-REQ-018 | verifies | VER-REQ-061 verifies the SIL-3 PAT qualification enforcement system requirement | SIL-3 H-004: PAT model must be qualified before accepting spectral data for release decisions; lapsed qualification creates undetected OOS risk | 2026-03-25T18:39:09.243Z
VER-REQ-047 | SUB-REQ-031 | verifies | VER-REQ-047 verifies the SIL-3 HFT≥1 architectural redundancy requirement for PAT CQA evaluation | SIL-3 H-004: architecture requirement mandates dual-channel CQA evaluation; failover test is definitive evidence of SIL-3 architectural achievement | 2026-03-25T18:39:08.534Z
SYS-REQ-012 | ARC-REQ-004 | derives | SYS-REQ-012 in-process rejection requirements drive tablet compression decomposition | Four-component compression decomposition derived from force rejection and containment requirements | 2026-03-25T17:43:32.555Z
SYS-REQ-001 | ARC-REQ-003 | derives | SYS-REQ-001 throughput requirements drive linear G&B process train topology | Linear G&B process train derived from throughput and process control requirements | 2026-03-25T17:43:31.875Z
SYS-REQ-002 | ARC-REQ-002 | derives | SYS-REQ-002 EBR integrity requirements drive MES five-module decomposition | MES decomposition derived from EBR cryptographic hash chain and signature requirements | 2026-03-25T17:43:31.097Z
SYS-REQ-003 | ARC-REQ-001 | derives | SYS-REQ-003 PAT requirements drive three-instrument PAT decomposition architecture | Three-instrument PAT architecture with centralised DAC Workstation is derived from multi-analyte CQA monitoring requirements | 2026-03-25T17:43:22.848Z
SYS-REQ-003 | SUB-REQ-031 | derives | SYS-REQ-003 PAT response time requirements derive hardware architecture constraint SUB-REQ-031 | SIL-3 allocation on the CQA diversion function demands HFT=1 architecture; single-channel DAC cannot achieve SIL-3 per IEC 61508 Table 2 | 2026-03-25T17:40:39.488Z
VER-REQ-046 | SYS-REQ-008 | verifies | VER-REQ-046 verifies MES-guided changeover workflow and electronic release gate | SYS-REQ-008 MES workflow guidance and sign-off gate have no other VER entry; Scenario 5 qualification evidence for H-002 | 2026-03-25T17:38:58.105Z
VER-REQ-045 | SYS-REQ-006 | verifies | VER-REQ-045 verifies system-level cleanroom environmental alarm and halt response times | EU GMP Annex 1 requires all three environmental parameters tested at system level; IFC-016 interface test is insufficient | 2026-03-25T17:38:57.418Z
VER-REQ-044 | SYS-REQ-005 | verifies | VER-REQ-044 verifies system-level emergency stop timing across all three activation paths | System-level E-stop qualification covering H-001/H-003/H-007; subsystem tests cannot demonstrate coordinated multi-system stop | 2026-03-25T17:38:48.854Z
VER-REQ-015 | SUB-REQ-016 | verifies | VER-REQ-015 verifies complete G&B cycle from API charge to IBC seal meeting all CQA specifications | End-to-end G&B integration test is the process validation Stage 2 sign-off test; SUB-REQ-016 is the primary granulation endpoint control requirement | 2026-03-25T17:35:50.054Z
VER-REQ-009 | IFC-REQ-001 | verifies | VER-REQ-009 verifies the end-to-end PAT-to-diversion chain cumulative latency | End-to-end chain test is the definitive SIL-3 H-004 safety case evidence; IFC-REQ-001 is the primary CQA alarm interface in the chain | 2026-03-25T17:35:49.356Z
VER-REQ-027 | IFC-REQ-011 | verifies | VER-REQ-027 verifies rejection events and state transitions are written to MES EBR within latency bound | Links 55-event injection test to the 21 CFR Part 11 compliant rejection event logging interface requirement | 2026-03-25T17:35:48.680Z
VER-REQ-026 | IFC-REQ-010 | verifies | VER-REQ-026 verifies IPC OPC-UA data stream rate, timestamp accuracy, and channel completeness | Links 30-minute OPC-UA monitoring test to the tablet compression IPC data interface requirement | 2026-03-25T17:35:47.999Z
VER-REQ-025 | SUB-REQ-028 | verifies | VER-REQ-025 verifies tablet compression containment pressure differential and alarm response SUB-REQ-028 | Links exhaust-port-block containment failure test to H-001 airborne potent compound exposure prevention | 2026-03-25T17:35:34.253Z
VER-REQ-024 | SUB-REQ-027 | verifies | VER-REQ-024 verifies tablet press guard interlock and LOTO restart prevention SUB-REQ-027 | Links guard-door opening stop-time test to SIL-2 H-007 mechanical safety interlock requirement | 2026-03-25T17:35:33.571Z
VER-REQ-023 | SUB-REQ-024 | verifies | VER-REQ-023 verifies PAT channel degradation response timing and two-sensor safe state SUB-REQ-024 | Links single-channel fault injection test to the multi-channel degraded-mode performance threshold requirement | 2026-03-25T17:35:32.870Z
VER-REQ-022 | IFC-REQ-009 | verifies | VER-REQ-022 verifies degraded-mode transition latency and CQA continuity on IFC-REQ-009 | Links NIR-sensor-disable test to the quantified degraded-mode protocol interface requirement | 2026-03-25T17:35:32.155Z
VER-REQ-021 | SUB-REQ-001 | verifies | VER-REQ-021 verifies NIR spectrometer spectral range and SNR in production simulation SUB-REQ-001 | Links 100-consecutive-spectrum acquisition test to the primary CQA sensor performance specification | 2026-03-25T17:35:14.698Z
VER-REQ-020 | SUB-REQ-020 | verifies | VER-REQ-020 verifies IBC blend uniformity acceptance criterion SUB-REQ-020 | Links stratified HPLC confirmation test to the ICH Q2(R1) blend uniformity RSD requirement | 2026-03-25T17:35:13.994Z
VER-REQ-019 | SUB-REQ-009 | verifies | VER-REQ-019 verifies EBR tamper detection via direct DB modification SUB-REQ-009 | Links dual-path (API and DB) tamper test to 21 CFR Part 11 audit trail integrity requirement | 2026-03-25T17:35:13.307Z
VER-REQ-018 | IFC-REQ-004 | verifies | VER-REQ-018 verifies real-time CQA measurement stream latency on PAT-to-MES interface IFC-REQ-004 | Links OOS injection end-to-end latency test to the safety-critical CQA data interface requirement | 2026-03-25T17:35:12.619Z
VER-REQ-017 | IFC-REQ-002 | verifies | VER-REQ-017 verifies PAT-to-MES sensor health status OPC-UA update IFC-REQ-002 | Links NIR attenuation injection test to the early-warning sensor degradation signal interface | 2026-03-25T17:35:01.933Z
VER-REQ-016 | IFC-REQ-008 | verifies | VER-REQ-016 verifies IBC handoff seal inspection and batch genealogy record IFC-REQ-008 | Links IBC tamper-evidence inspection and genealogy record verification to the G&B-to-compression transfer interface | 2026-03-25T17:35:01.241Z
VER-REQ-014 | IFC-REQ-007 | verifies | VER-REQ-014 verifies MES-to-G&B recipe delivery and EBR feedback latency IFC-REQ-007 | Links PLC setpoint acknowledgment timing test to the recipe interface response requirement | 2026-03-25T17:35:00.576Z
VER-REQ-013 | IFC-REQ-006 | verifies | VER-REQ-013 verifies G&B-to-PAT NIR interface data integrity and latency IFC-REQ-006 | Links parallel-reference-spectrometer integration test to the LOD measurement interface requirement | 2026-03-25T17:34:59.905Z
VER-REQ-012 | SUB-REQ-015 | verifies | VER-REQ-012 verifies MES paper backup mode switchover on data integrity failure SUB-REQ-015 | Links hash chain injection demonstration to the SIL-2 H-006 safe-state paper backup requirement | 2026-03-25T17:34:48.584Z
VER-REQ-011 | SUB-REQ-007 | verifies | VER-REQ-011 verifies laser diffraction analyser accuracy and repeatability SUB-REQ-007 | Links NIST SRM 1018c reference measurement test to the particle size analyser qualification requirement | 2026-03-25T17:34:47.899Z
VER-REQ-010 | SUB-REQ-002 | verifies | VER-REQ-010 verifies Raman spectrometer spectral range and resolution SUB-REQ-002 | Links NIST SRM 1921b reference scan test to the Raman spectrometer performance specification | 2026-03-25T17:34:47.224Z
VER-REQ-008 | SUB-REQ-010 | verifies | VER-REQ-008 verifies EBR hash chain integrity detection SUB-REQ-010 | Links 500-entry hash chain tamper test to the SIL-2 H-006 EBR integrity requirement | 2026-03-25T17:34:46.541Z
VER-REQ-007 | SUB-REQ-011 | verifies | VER-REQ-007 verifies MES LOTO restart prevention requirement SUB-REQ-011 | Links LOTO registry lock test to the SIL-2 H-007 mechanical entrapment prevention requirement | 2026-03-25T17:34:34.801Z
VER-REQ-006 | SUB-REQ-008 | verifies | VER-REQ-006 verifies 21 CFR Part 11 authentication enforcement on EBR critical actions | Links unauthenticated-action rejection test to the MES 21 CFR Part 11 electronic signature requirement | 2026-03-25T17:34:34.165Z
VER-REQ-005 | IFC-REQ-003 | verifies | VER-REQ-005 verifies MES diversion acknowledgment latency on IFC-REQ-003 | Links 20-event acknowledgment timing test to the MES-to-PAT confirmation interface requirement | 2026-03-25T17:34:33.474Z
VER-REQ-004 | IFC-REQ-001 | verifies | VER-REQ-004 verifies CQA alarm transit time and loss rate on PAT-MES OPC-UA interface | Links 100-event soak test to SIL-3 alarm delivery requirement on the primary diversion trigger interface | 2026-03-25T17:34:32.812Z
VER-REQ-003 | SUB-REQ-005 | verifies | VER-REQ-003 verifies sensor degradation detection requirement SUB-REQ-005 | Links SNR attenuation injection test to the SIL-3 sensor health monitoring requirement | 2026-03-25T17:34:21.505Z
VER-REQ-002 | SUB-REQ-004 | verifies | VER-REQ-002 verifies diversion valve actuation time requirement SUB-REQ-004 | Links pneumatic solenoid spring-return test to the SIL-3 H-004 valve response requirement | 2026-03-25T17:34:20.842Z
VER-REQ-001 | SUB-REQ-003 | verifies | VER-REQ-001 verifies NIR model evaluation latency requirement SUB-REQ-003 | Establishes formal traceability from verification test to the SIL-3 CQA model latency requirement it exercises | 2026-03-25T17:34:20.120Z
VER-REQ-043 | SUB-REQ-030 | verifies | VER-043 verifies SUB-030 IPC degraded mode response across all three channel failures | VER-043 exercises all three IPC channel failure modes and verifies the 60% throughput limit and 5-minute manual sampling cadence required by SUB-REQ-030. | 2026-03-25T17:06:57.340Z
VER-REQ-042 | SUB-REQ-029 | verifies | VER-042 verifies SUB-029 RFID tooling lifecycle gate and read-failure block | VER-042 tests both tooling lifecycle limit and RFID read failure press-block required by SUB-REQ-029. | 2026-03-25T17:06:56.652Z
VER-REQ-041 | SUB-REQ-025 | verifies | VER-041 verifies SUB-025 compression force rejection gate and timing | VER-041 verifies the 200 ms ejection response and ±5 kN force gate with 100% sensitivity and specificity required by SUB-REQ-025. | 2026-03-25T17:06:55.969Z
VER-REQ-040 | SUB-REQ-022 | verifies | VER-040 verifies SUB-022 PAT-unavailable degraded blend safety gate | VER-040 exercises the PAT-unavailable degraded blending path, including the supervisory authorisation gate and fixed-time blend minimum, required by SUB-REQ-022. | 2026-03-25T17:06:55.300Z
VER-REQ-039 | SUB-REQ-016 | verifies | VER-039 verifies SUB-016 HSG endpoint response timing | VER-039 measures the 10-second endpoint stop-and-transfer response required by SUB-REQ-016 across three consecutive runs. | 2026-03-25T17:06:54.650Z
VER-REQ-038 | SUB-REQ-014 | verifies | VER-038 verifies SUB-014 EBR backup interval and restore time | VER-038 measures the 15-minute backup interval and 30-minute RTO specified in SUB-REQ-014 for H-006 EBR data integrity failure recovery. | 2026-03-25T17:06:40.158Z
VER-REQ-037 | SUB-REQ-012 | verifies | VER-037 verifies SUB-012 LOTO event logging completeness | VER-037 tests all four LOTO event types including the safety-critical override-denial path required by SUB-REQ-012 for H-007 mitigation. | 2026-03-25T17:06:39.409Z
VER-REQ-036 | IFC-REQ-020 | verifies | VER-036 verifies IFC-020 LIMS batch release interface | VER-REQ-036 verifies the closed-loop LIMS-MES release workflow and batch disposition block of IFC-REQ-020. | 2026-03-25T16:10:03.003Z
VER-REQ-035 | IFC-REQ-019 | verifies | VER-035 verifies IFC-019 ERP production order interface | VER-REQ-035 verifies the ERP production order authority chain and timing requirements of IFC-REQ-019. | 2026-03-25T16:10:02.315Z
VER-REQ-034 | IFC-REQ-018 | verifies | VER-034 verifies IFC-018 material identity gate | VER-REQ-034 verifies the secondary barcode identity verification and reject gate of IFC-REQ-018 at the Material Handling to Granulation charge point. | 2026-03-25T16:10:01.611Z
VER-REQ-033 | IFC-REQ-017 | verifies | VER-033 verifies IFC-017 dispensing interface | VER-REQ-033 verifies the 60-second EBR write and GMP deviation gate of IFC-REQ-017 for the Material Handling to MES dispensing interface. | 2026-03-25T16:10:00.912Z
VER-REQ-032 | IFC-REQ-016 | verifies | VER-032 verifies IFC-016 containment halt timing | VER-REQ-032 verifies the 30-second halt response and EBR deviation recording of IFC-REQ-016 for the Containment to MES environmental monitoring interface. | 2026-03-25T16:10:00.211Z
VER-REQ-031 | IFC-REQ-015 | verifies | VER-031 verifies IFC-015 coating release gate | VER-REQ-031 verifies the coating release record interlock gate of IFC-REQ-015 at the Film Coating to Packaging transfer boundary. | 2026-03-25T16:09:48.443Z
VER-REQ-030 | IFC-REQ-014 | verifies | VER-030 verifies IFC-014 packaging serialisation | VER-REQ-030 verifies the serialisation reconciliation timing and production order block of IFC-REQ-014. | 2026-03-25T16:09:47.731Z
VER-REQ-029 | IFC-REQ-013 | verifies | VER-029 verifies IFC-013 transfer gate | VER-REQ-029 verifies the accept/reject gate logic of IFC-REQ-013 at the Tablet Compression to Film Coating transfer boundary. | 2026-03-25T16:09:47.015Z
VER-REQ-028 | IFC-REQ-012 | verifies | VER-028 verifies IFC-012 Film Coating MES timing | VER-REQ-028 is the test procedure that verifies IFC-REQ-012 timing and EBR data completeness requirements for the Film Coating to MES interface. | 2026-03-25T16:09:46.309Z
SYS-REQ-002 | SUB-REQ-029 | derives | Punch RFID tooling tracking derives from EBR system requirement | SYS-REQ-002 requires electronic batch records for all GMP-critical activities; SUB-REQ-029 implements electronic tracking of punch tooling usage count and read failures as part of the batch record — 21 CFR Part 11 mandates electronic records for maintenance activities affecting product quality. | 2026-03-25T15:14:43.858Z
SYS-REQ-002 | IFC-REQ-011 | derives | TC-to-MES batch record write derives from electronic batch record system requirement | SYS-REQ-002 requires EBR generation and archival for all batches; IFC-REQ-011 specifies the tablet press's contribution to that record — rejection events and subsystem state changes are mandatory EBR entries under 21 CFR Part 11. | 2026-03-25T15:10:00.670Z
SYS-REQ-003 | IFC-REQ-010 | derives | IPC-to-PAT OPC-UA interface derives from system PAT data acquisition requirement | SYS-REQ-003 requires PAT sensor data at 30s intervals; IFC-REQ-010 adds the IPC tablet-level data stream that supplements NIR with physical property measurements — the tablet press is a PAT data source within the system-level PAT requirement. | 2026-03-25T15:09:59.897Z
SYS-REQ-009 | SUB-REQ-030 | derives | IPC degraded mode operation derives from system-level degraded production requirement | SYS-REQ-009 requires continued production with increased sampling when a non-critical fault is detected; SUB-REQ-030 implements this at the tablet press by specifying the 60% RPM cap and 5-minute manual sampling interval — the press-specific implementation of that degraded production policy. | 2026-03-25T15:08:51.796Z
SYS-REQ-004 | SUB-REQ-028 | derives | SYS OEL pressure isolation derives to SUB containment housing setpoint | SUB-REQ-028 (-15 Pa containment housing) exists because SYS-REQ-004 mandates negative pressure isolation for OEB 3-5 compounds; the -15 Pa subsystem setpoint is derived from the system-level H-001 containment integrity requirement, providing the specific pressure floor that implements potent compound airborne exposure prevention. | 2026-03-25T15:08:51.106Z
SYS-REQ-011 | SUB-REQ-027 | derives | SYS LOTO enforcement derives to SUB tablet press guard interlock | SUB-REQ-027 (guard door opening triggers tablet press de-energisation within 0.5 s) exists because SYS-REQ-011 mandates electronic LOTO enforcement preventing equipment re-energisation during maintenance; the guard interlock directly implements the SIL-2 LOTO safety gate at the Tablet Compression Subsystem level. | 2026-03-25T15:08:50.445Z
SYS-REQ-012 | SUB-REQ-026 | derives | IPC fill-depth servo feedback derives from automated quality enforcement | SYS-REQ-012 requires automated in-process enforcement; SUB-REQ-026 provides the upstream fill-depth control loop that keeps tablets within spec — the preventive control mechanism for the same quality objective. | 2026-03-25T15:08:49.801Z
SYS-REQ-012 | SUB-REQ-025 | derives | SYS tablet rejection derives to SUB punch force monitoring | SUB-REQ-025 (per-station punch force monitoring with automatic rejection) exists because SYS-REQ-012 mandates automated in-process rejection of out-of-specification tablets; the compression force monitoring provides the primary weight-surrogate measurement that operationalises the system-level tablet quality rejection capability. | 2026-03-25T15:08:49.144Z
STK-REQ-006 | SYS-REQ-002 | derives | EU GMP Annex 11 EBR compliance obligation drives SYS EBR generation requirement | STK-REQ-006 also invokes EU GMP Annex 11 (computerised systems), which requires EBR audit trails, electronic signatures, and data integrity controls. SYS-REQ-002 is the system-level response to this Annex 11 obligation. | 2026-03-25T14:38:47.501Z
SYS-REQ-009 | SUB-REQ-024 | derives | SYS-REQ-009 degraded mode derives to quantified PAT sensor-degraded performance floor | SYS-REQ-009 requires PAT to switch to manual testing mode when sensor-degraded. SUB-REQ-024 is the quantified subsystem implementation, adding the 10-second suspension window, 2-of-3 channel minimum floor, 60-second prompt window, and 30-second EBR submission window that make the degraded mode behaviour testable and auditable. | 2026-03-25T14:12:21.055Z
SYS-REQ-009 | IFC-REQ-009 | derives | SYS-REQ-009 degraded mode requirement derives to quantified MES-PAT degraded mode interface | SYS-REQ-009 requires MES-coordinated manual sampling during PAT degraded mode. IFC-REQ-009 is the quantified interface specification that implements this coordination, adding the 30-second command delivery window, minimum 3 CQA parameter floor, and 5-minute confirmation receipt requirement. | 2026-03-25T14:12:09.894Z
STK-REQ-006 | SYS-REQ-002 | derives | Regulatory compliance requirement derives EBR system requirement | STK-REQ-006 mandates compliance with FDA 21 CFR Part 11, EU GMP Annex 15, and ICH Q10. SYS-REQ-002 is the primary system mechanism for compliance: the EBR engine with electronic signatures, access controls, and audit trails directly implements the 21 CFR Part 11 obligation. This is the highest-coupling derivation path from the compliance stakeholder requirement. | 2026-03-25T14:07:42.518Z
SYS-REQ-007 | IFC-REQ-008 | derives | IBC sealed handoff implements batch genealogy chain at G&B-to-compression boundary | REQ-020 requires full batch genealogy across the production sequence. IFC-REQ-008 specifies the sealed IBC handoff protocol that maintains genealogy chain integrity at the G&B-to-compression boundary. | 2026-03-25T11:45:33.104Z
SYS-REQ-001 | SUB-REQ-018 | derives | FBD temperature control implements CPP control for drying step in production sequence | REQ-014 requires the system to operate the drying step in the production sequence. SUB-REQ-018 specifies the FBD inlet air temperature CPP control requirement, which is the primary process parameter controlling the drying step outcome. | 2026-03-25T11:45:32.433Z
SYS-REQ-004 | SUB-REQ-023 | derives | G&B containment implements negative pressure isolation at transfer points | REQ-017 requires negative pressure isolation for OEB4/5 compounds. SUB-REQ-023 extends this to OEB3 and specifies the G&B-specific exposure limit for inter-vessel transfers, which are the highest-risk containment points in the G&B subsystem. | 2026-03-25T11:42:53.217Z
SYS-REQ-009 | SUB-REQ-022 | derives | G&B degraded blend mode is the G&B-specific implementation of PAT degraded mode | REQ-022 requires the system to switch to manual in-process testing when PAT enters degraded mode. SUB-REQ-022 specifies how G&B specifically responds to PAT NIR loss — using fixed-time blend with supervisory authorisation, which is the G&B-specific manual testing path. | 2026-03-25T11:42:52.577Z
SYS-REQ-007 | SUB-REQ-021 | derives | Mass balance accountability implements batch genealogy tracking at G&B level | REQ-020 requires full batch genealogy linking raw materials to finished product. SUB-REQ-021 implements this at the G&B subsystem level by tracking mass at each transfer point, forming the G&B contribution to the genealogy chain. | 2026-03-25T11:42:51.932Z
SYS-REQ-003 | SUB-REQ-020 | derives | IBC NIR blend endpoint integrates PAT data acquisition into blend control | REQ-016 mandates PAT sensor data evaluation for CQA model decisions. SUB-REQ-020 specifies the IBC blend endpoint as a PAT NIR decision, making it a direct application of REQ-016 to the blending operation. | 2026-03-25T11:42:51.295Z
SYS-REQ-001 | SUB-REQ-019 | derives | Sizing Mill PSD implements granule sizing step in production sequence | REQ-014 includes sizing as a production sequence step. SUB-REQ-019 specifies the PSD acceptance criterion for mill output, implementing REQ-014's sizing step. | 2026-03-25T11:42:50.625Z
SYS-REQ-001 | SUB-REQ-017 | derives | FBD LOD drying endpoint implements drying step in production sequence | REQ-014 includes drying as a production sequence step. SUB-REQ-017 quantifies the LOD acceptance criterion for FBD output, directly implementing REQ-014's drying step. | 2026-03-25T11:42:49.968Z
SYS-REQ-003 | SUB-REQ-016 | derives | PAT NIR wet-mass endpoint integrates G&B endpoint detection with PAT subsystem | REQ-016 requires PAT sensor data acquisition and CQA model evaluation; SUB-REQ-016 specifies how the PAT NIR wet-mass output is used by G&B to trigger endpoint — it exists because REQ-016 mandates real-time PAT integration into process control decisions. | 2026-03-25T11:42:32.912Z
SYS-REQ-001 | SUB-REQ-016 | derives | Granulation endpoint detection implements production sequence step control | REQ-014 requires the system to operate the production sequence through granulation; SUB-REQ-016 defines the specific endpoint criterion and timing for the granulation step, making it a direct functional decomposition of REQ-014's granulation sequencing. | 2026-03-25T11:42:32.191Z
SYS-REQ-007 | IFC-REQ-004 | derives | SYS batch genealogy → IFC PAT CQA data stream to MES for process parameter logging | SYS-020 requires linking finished product to process parameter logs — the PAT-to-MES CQA data stream provides the quality parameter dimension | 2026-03-25T10:36:57.937Z
SYS-REQ-007 | SUB-REQ-013 | derives | SYS batch genealogy → SUB MES genealogy database with multi-dimensional query | SYS-020 4-hour recall scope determination allocates to MES batch genealogy database as the aggregation point for all traceability dimensions | 2026-03-25T10:36:57.239Z
SYS-REQ-011 | SUB-REQ-012 | derives | SYS LOTO event logging → SUB MES LOTO event recording in EBR | SYS-024 mandates logging with operator ID, timestamp, equipment ID — these fields drive the LOTO event schema in MES | 2026-03-25T10:36:56.537Z
SYS-REQ-011 | SUB-REQ-011 | derives | SYS electronic lockout → SUB MES real-time lockout registry with restart prevention | SYS-024 electronic lockout verification requirement allocates to MES as the equipment state authority | 2026-03-25T10:36:55.809Z
SYS-REQ-002 | SUB-REQ-014 | derives | SYS EBR 15-minute backup → SUB MES automated backup with integrity verification | SYS-015 15-minute backup interval allocates directly to the MES backup subsystem function | 2026-03-25T10:36:49.675Z
SYS-REQ-002 | SUB-REQ-010 | derives | SYS EBR cryptographic hash → SUB MES SHA-256 hash chain with discontinuity detection | SYS-015 cryptographic hash on every write allocates directly to MES hash chain implementation | 2026-03-25T10:36:49.014Z
SYS-REQ-002 | SUB-REQ-009 | derives | SYS EBR compliance derives to SUB MES audit trail | SUB-REQ-009 (tamper-evident MES audit trail for EBR events) exists because SYS-REQ-002 mandates 21 CFR Part 11 compliant EBRs with electronic signatures; audit trail completeness is a primary Part 11 compliance element, making the MES audit trail sub-requirement a direct derivation of the system-level EBR requirement. | 2026-03-25T10:36:48.357Z
SYS-REQ-002 | SUB-REQ-008 | derives | SYS EBR electronic signatures → SUB MES 21 CFR Part 11 e-signature enforcement | SYS-015 electronic signature requirement allocates to MES as the EBR owner and signature authority | 2026-03-25T10:36:47.722Z
SYS-REQ-009 | IFC-REQ-005 | derives | SYS degraded-mode manual sampling → IFC MES-to-PAT manual sampling schedule command | SYS-022 requires MES-coordinated manual sampling during degraded mode, driving this bidirectional interface requirement | 2026-03-25T10:36:42.971Z
SYS-REQ-009 | IFC-REQ-002 | derives | SYS degraded-mode transition → IFC sensor health status reporting interface | SYS-022 30-second detection requirement drives the 10-second health reporting interval to MES for trend-based degradation detection | 2026-03-25T10:36:42.272Z
SYS-REQ-009 | SUB-REQ-006 | derives | SYS degraded-mode manual sampling → SUB PAT degraded mode with 15-minute sampling prompts | SYS-022 15-minute manual sampling and 50% throughput requirements directly allocate to PAT degraded-mode operation | 2026-03-25T10:36:41.602Z
SYS-REQ-009 | SUB-REQ-005 | derives | SYS degraded-mode transition → SUB sensor self-diagnostics and 15-second detection | SYS-022 30-second degraded-mode switching requirement allocates 15 seconds to PAT sensor self-diagnosis | 2026-03-25T10:36:40.842Z
SYS-REQ-003 | SUB-REQ-001 | derives | SYS PAT data acquisition derives to SUB NIR spectrometer spec | SUB-REQ-001 (NIR spectrometer diffuse reflectance at 256 wavelengths, 1 Hz) exists because SYS-REQ-003 mandates PAT data acquisition at defined intervals; the NIR instrument sub-requirement provides the primary CQA sensor implementation from which the system-level PAT monitoring capability derives. | 2026-03-25T10:36:34.846Z
SYS-REQ-003 | SUB-REQ-004 | derives | SYS diversion actuation → SUB diversion valve with position feedback | SYS-016 2-second valve actuation requirement allocates directly to the PAT subsystem diversion valve function | 2026-03-25T10:36:34.108Z
SYS-REQ-003 | SUB-REQ-003 | derives | SYS PAT model evaluation timing → SUB CQA model evaluation with integrity checks | SYS-016 5-second model evaluation requirement directly allocates to the PAT subsystem CQA model processing pipeline | 2026-03-25T10:36:33.427Z
SYS-REQ-003 | IFC-REQ-001 | derives | SYS PAT acquisition and diversion → IFC CQA alarm signal specification | SYS-016 2-second diversion window drives the 500ms latency budget for the PAT-to-MES CQA alarm interface | 2026-03-25T10:36:32.636Z
STK-REQ-013 | SYS-REQ-012 | derives | Pharmacopoeial tablet specification compliance drives automated in-process rejection with defined tolerances | STK-REQ-013 requires finished products to comply with pharmacopoeial specifications for tablet weight, hardness, friability, and dissolution. SYS-REQ-012 exists because achieving pharmacopoeial compliance requires automated in-process rejection — manual 100% inspection is not feasible at production rates, and SYS-REQ-012 specifies the rejection thresholds derived from the pharmacopoeial limits. | 2026-03-25T10:17:40.217Z
STK-REQ-012 | SYS-REQ-011 | derives | LOTO safety requirement drives system-enforced electronic lockout registry with restart prevention | STK-REQ-012 requires documented LOTO procedures and physical isolation for all equipment maintenance. SYS-REQ-011 exists because physical LOTO alone does not prevent accidental electronic restart — the system must enforce a software lockout registry that blocks restart commands while a maintenance lock is registered, satisfying the 'no energisation during lockout' safety obligation. | 2026-03-25T10:17:39.538Z
STK-REQ-008 | SYS-REQ-010 | derives | DSCSA/EU FMD serialisation mandate drives automated DataMatrix barcode application requirement | STK-REQ-008 requires 100% serialisation with unique identifiers per the Drug Supply Chain Security Act (DSCSA) and EU FMD. SYS-REQ-010 exists because these regulations specify DataMatrix format encoding GTIN, serial number, lot, and expiry, applied by the system to every finished product unit — human-applied serialisation cannot meet the 100% and anti-counterfeiting requirements. | 2026-03-25T10:17:38.842Z
STK-REQ-009 | SYS-REQ-009 | derives | Degraded-mode production continuity drives PAT fallback to manual in-process testing specification | STK-REQ-009 requires production to continue in degraded mode when a non-critical PAT sensor fault is detected. SYS-REQ-009 exists because 'continued production' requires a defined fallback mode (switching to manual in-process testing at specified frequency) — without a specified fallback, the system cannot maintain compliance during PAT outage. | 2026-03-25T10:17:38.197Z
STK-REQ-007 | SYS-REQ-008 | derives | Validated changeover and cross-contamination limit drives system-guided cleaning verification requirement | STK-REQ-007 requires validated changeover with cross-contamination residue levels below safety thresholds. SYS-REQ-008 exists because achieving this requires the system to guide operators through the validated cleaning sequence, verify cleaning completion with checks, and prevent production restart until cleaning sign-off — procedural guidance without system enforcement does not satisfy the validation requirement. | 2026-03-25T10:17:37.573Z
STK-REQ-010 | SYS-REQ-007 | derives | Bidirectional material traceability requirement drives batch genealogy database with complete linkage | STK-REQ-010 requires full bidirectional traceability from raw material to finished product (and reverse). SYS-REQ-007 exists because this requires the system to maintain a batch genealogy database with the linking structure — bidirectionality is only possible if every material charge and transfer event is captured in a queryable record. | 2026-03-25T10:17:36.923Z
STK-REQ-011 | SYS-REQ-006 | derives | ISO Class 7 GMP cleanroom specification drives continuous environmental monitoring with alarm thresholds | STK-REQ-011 specifies ISO Class 7 (EU GMP Grade C) cleanroom conditions for Normal Production mode. SYS-REQ-006 exists because maintaining ISO Class 7 requires the system to continuously monitor temperature (20±2°C), RH (45±10%), differential pressure (≥15 Pa), and particle count, and to alarm on exceedance — periodic manual monitoring cannot guarantee continuous compliance. | 2026-03-25T10:17:36.302Z
STK-REQ-005 | SYS-REQ-005 | derives | Emergency stop safety need drives controlled de-energisation time limit and ordered shutdown | STK-REQ-005 requires full controlled stop on emergency condition detection. SYS-REQ-005 exists because the 'controlled' qualifier demands a defined maximum de-energisation time (500 ms) and ordered shutdown sequence — an uncontrolled power-cut would not meet the safety requirement for personnel and equipment protection. | 2026-03-25T10:17:35.664Z
STK-REQ-004 | SYS-REQ-004 | derives | OEB 4/5 potent compound containment drives active negative-pressure enclosure requirement | STK-REQ-004 requires containment of potent compounds with OEL <1 µg/m³ (OEB 4/5). SYS-REQ-004 exists because this exposure limit can only be achieved through negative-pressure enclosures with HEPA exhaust — the system must actively maintain and monitor containment rather than rely on passive measures. | 2026-03-25T10:17:34.981Z
STK-REQ-003 | SYS-REQ-003 | derives | PAT real-time QA monitoring need drives multi-modal sensor acquisition and CQA model evaluation | STK-REQ-003 requires continuous real-time in-process quality monitoring via PAT. SYS-REQ-003 exists because this stakeholder need requires the system to acquire spectra from three sensor modalities at a defined interval, run CQA chemometric models, and trigger diversion — these are inseparable system functions. | 2026-03-25T10:17:14.745Z
STK-REQ-002 | SYS-REQ-002 | derives | 21 CFR Part 11 EBR compliance mandate drives system-level EBR generation and archival | STK-REQ-002 mandates FDA 21 CFR Part 11 and EU Annex 11 EBR compliance. SYS-REQ-002 exists because these regulations require the system itself to generate, execute, and archive records with electronic signatures and audit trails — compliance cannot be delegated to a separate record system. | 2026-03-25T10:17:14.008Z
STK-REQ-001 | SYS-REQ-001 | derives | OEE target drives full-sequence production orchestration requirement | STK-REQ-001 mandates OEE ≥75% across the full production cycle. SYS-REQ-001 exists because achieving this OEE requires the system to orchestrate and control every step from raw material dispense through to packaged product — throughput cannot be measured without system ownership of the sequence. | 2026-03-25T10:17:13.357Z

## Linksets
Source Document | Target Document | Default Link Type | Link Count
subsystem-requirements | verification-requirements |  | 89
interface-requirements | verification-requirements |  | 34
system-requirements | verification-requirements |  | 32
system-requirements | subsystem-requirements |  | 43
system-requirements | interface-requirements |  | 8
stakeholder-requirements | system-requirements |  | 30

## Sections
Document | Section | Short Code | Order | Requirements
architecture-decisions | Architecture Decisions | ARC | 0 | 11
interface-requirements | Interface Requirements | IFC | 0 | 20
stakeholder-requirements | Stakeholder Requirements | STK | 0 | 13
subsystem-requirements | Subsystem Requirements | SUB | 0 | 63
system-requirements | System Requirements | SYS | 0 | 29
verification-requirements | Verification Requirements | VER | 0 | 109