## Documents
Slug | Name | Short Code | Sections | Requirements | Created
architecture-decisions | Architecture Decisions | ARC | 1 | 11 | 2026-03-22T14:32:43.969Z
interface-requirements | Interface Requirements | IFC | 1 | 42 | 2026-03-22T14:32:43.687Z
stakeholder-requirements | Stakeholder Requirements | STK | 1 | 16 | 2026-03-22T14:32:43.400Z
subsystem-requirements | Subsystem Requirements | SUB | 1 | 95 | 2026-03-22T14:32:43.825Z
system-requirements | System Requirements | SYS | 1 | 20 | 2026-03-22T14:32:43.541Z
verification-requirements | Verification Requirements | VER | 1 | 62 | 2026-03-22T14:32:44.118Z

## Requirements
Ref | Text | Document | Section | Pattern | Verification | QA Score | Compliance | Rationale | Tags
ARC-REQ-001 | ARC: Safety Interlock Subsystem — Implemented as hardware-independent relay/safety-PLC chain, not as software functions within the supervisory controller. Alternatives considered: (1) software-only interlocks in supervisory controller — rejected because SIL 3 requires hardware independence per IEC 61508 clause 7.4.2.2 and H-007 cyber compromise scenario makes software-only unacceptable; (2) safety PLC with software-only voting — rejected because dual-NDIR sensor voting at hardware level provides better diagnostic coverage. Constraint: IEC 62443 defence-in-depth and IEC 61508 SIL 3 architectural constraints require physically separate safety channel. | architecture-decisions | Architecture Decisions |  | Analysis | 43 |  | H-001 (CO2 asphyxiation, SIL 3) and H-007 (cyber compromise) together mandate that the safety function cannot share hardware or software with the operational controller. The 150-year MTTFd target drives the choice of proven relay technology over complex programmable safety systems. | architecture, safety-interlock, session-462, idempotency:arc-safety-interlock-462
ARC-REQ-002 | ARC: Zone Controller Network — Distributed architecture with one dedicated controller per zone rather than centralised I/O. Each zone controller executes local PID loops and stores crop recipes for autonomous operation. Alternatives considered: (1) centralised controller with remote I/O racks — rejected because single point of failure would lose all zones simultaneously, and 72-hour network resilience requirement demands local recipe storage; (2) redundant centralised pair — rejected because cost exceeds distributed approach for 8 zones while providing worse zone isolation during faults. | architecture-decisions | Architecture Decisions |  | Analysis | 57 |  | The HVAC Failure and network resilience scenarios demonstrate that zone independence is critical — a fault in one zone must not cascade to others. Distributed architecture provides natural fault isolation boundaries aligned with the physical growing zone boundaries. | architecture, zone-controller, session-462, idempotency:arc-zone-controllers-462
ARC-REQ-003 | ARC: CO2 Enrichment Subsystem — Separated from Climate Management despite both controlling atmospheric composition. CO2 enrichment has a distinct safety boundary (SIL 3), distinct supply chain (bulk liquid CO2 from external supplier), fail-closed solenoid valve architecture, and distinct regulatory certification path. Grouping with HVAC would dilute the safety boundary and complicate SIL allocation. The interface between CO2 enrichment and climate (ventilation coordination) is managed through the zone controller. | architecture-decisions | Architecture Decisions |  | Inspection | 57 |  | H-001 drives SIL 3 allocation on CO2 functions. Mixing SIL 3 and non-safety-rated HVAC functions in one subsystem would force the entire climate subsystem to SIL 3, increasing cost and certification effort with no safety benefit. Clean subsystem boundaries enable independent safety certification. | architecture, co2-enrichment, session-462, idempotency:arc-co2-separation-462
ARC-REQ-004 | ARC: Supervisory Control Subsystem — Energy optimisation function grouped with supervisory control rather than as a separate subsystem. Energy decisions (demand response, load curtailment, photoperiod scheduling) require crop priority context, facility-wide load visibility, and inter-zone coordination that only the supervisory controller possesses. A separate energy subsystem would duplicate the facility-wide state model. The OpenADR 2.0 interface is a protocol adapter within the supervisory platform. | architecture-decisions | Architecture Decisions |  | Analysis | 57 |  | Energy optimisation is decision-layer logic that coordinates across zones using the same data model as recipe management and mode transitions. Separating it would create a tight coupling between two subsystems sharing the same state, which is worse than consolidation. | architecture, supervisory, energy, session-462, idempotency:arc-supervisory-energy-462
ARC-REQ-005 | ARC: Data Acquisition and Compliance Subsystem — Separated from supervisory control despite data flowing through the same network. Compliance data requires cryptographic integrity chains, tamper-evident storage, and regulatory retention policies (2-year BRCGS) that impose different design constraints from operational data. A combined system would risk compliance requirements inflating the complexity of the real-time control path, or operational priorities compromising audit trail integrity. | architecture-decisions | Architecture Decisions |  | Inspection | 57 |  | Food Safety Auditor stakeholder requires independently verifiable records. If the operational controller can modify historical records, the audit trail is not tamper-evident. Physical and logical separation of the compliance data path from the control path provides defence-in-depth for data integrity. | architecture, compliance, session-462, idempotency:arc-data-compliance-462
ARC-REQ-006 | ARC: Nutrient Management Subsystem — Separated dosing control (Dosing Pump Array + EC/pH Sensor Array) from fluid distribution (Irrigation Controller + Zone Irrigation Valve Array + Recirculation Pump System) to isolate the SIL-2 chemical dosing chain from the lower-risk irrigation timing functions. Dosing-excess watchdog is implemented as a hardwired cumulative counter in the Dosing Pump Array drive firmware rather than as a software function in the Irrigation Controller, consistent with ARC-REQ-001 (safety-critical functions must not rely on software alone). Bulk chemical storage (Nutrient Reservoir and Mixing System) is passive and requires no safety integrity — its concentrate tanks are physical inventory only. The Recirculation Pump System uses a duty/standby configuration rather than a single high-capacity pump to eliminate single-point failure of nutrient delivery, recognising that pump failure for >15 minutes causes crop stress across all zones. | architecture-decisions | Architecture Decisions |  | Inspection | 57 |  | IEC 61508 SIL-2 allocation on the dosing chain (SYS-REQ-006, SYS-REQ-007) requires architectural separation between the safety-relevant dosing watchdog hardware and the non-safety irrigation scheduler. Mixing these in a single controller would require the entire irrigation controller to be SIL-2 qualified, disproportionate to the risk of timing functions alone. | architecture, nutrient-management-subsystem, session-466, idempotency:arc-nutrient-management-subsystem-466
ARC-REQ-007 | ARC: Horticultural Lighting Subsystem — Four-component architecture separating control intelligence (Lighting Control Unit) from power conversion (LED Driver Module Array), photon delivery (LED Fixture Array), and feedback sensing (PAR Sensor Array + Fixture Thermal Monitoring Array). Thermal protection is split: software thermal derating via LCU for gradual ramp-down above 75°C, and a hardwired comparator circuit in the Fixture Thermal Monitoring Array for SIL-2 hard trip at 85°C independent of any software path. This split avoids routing safety-critical shutdown through the control software, ensuring the thermal trip meets IEC 61508 SIL 2 without requiring the full LCU to be SIL-certified. DALI-2 chosen over 0-10V for dimming because it supports per-fixture status feedback, individual addressing, and fault reporting — essential for 400kW+ arrays where undetected driver failure would degrade PAR accuracy without indication. | architecture-decisions | Architecture Decisions |  | Inspection | 57 |  | Documents the architectural trade-off that separates thermal protection into two independent paths: LCU software for graceful derating and hardwired comparator for safety trip. This ensures SIL 2 compliance for the thermal interlock without raising the SIL requirement of the entire software control stack. The DALI-2 selection over 0-10V is justified by operational observability requirements in a large facility. | architecture, horticultural-lighting, session-467, idempotency:arc-horticultural-lighting-467
ARC-REQ-008 | ARC: Climate Management Subsystem — Five-component decomposition separating sensing, control logic, actuation, and ventilation. Zone Climate Controller issues setpoints via Modbus RTU to the HVAC Actuator Interface rather than directly commanding hardware: this isolates the PID control algorithm from HVAC variant differences (DX vs chilled water vs VRF) and allows controller replacement without rewiring. Temperature Sensor Network and Relative Humidity Sensor Array are kept as separate components because their calibration cycles, failure modes, and Safety Interlock connections differ. Fresh Air Ventilation Controller is decoupled from the main HVAC loop because it coordinates with CO2 Enrichment Subsystem and must remain operable when the compressor circuit is tripped. | architecture-decisions | Architecture Decisions |  | Inspection | 57 |  | Separation of Zone Climate Controller from HVAC Actuator Interface enables swapping HVAC plant type without controller modification. Separate Temperature Sensor Network and RH Sensor Array components reflect different IEC 61511 proof-test intervals and independent safety trip channels to Safety Interlock Subsystem. Fresh Air Ventilation Controller decoupled from main HVAC loop allows it to continue operating when the compressor circuit is tripped. | architecture, climate-management, session-469, idempotency:arc-climate-management-469
ARC-REQ-009 | ARC: Supervisory Control Subsystem — Five-component decomposition separating server infrastructure, recipe execution, operator interaction, demand response, and emergency sequencing. The Crop Recipe Engine is a separate component from the Plant Management Server because recipes must continue executing during server maintenance windows via a hot-standby recipe executor. The Emergency Shutdown Sequencer is isolated from the main supervisory bus with its own hardwired interface to the Safety Interlock Subsystem, ensuring shutdown can complete even if the network bus fails. The Demand Response Handler is decoupled from the Crop Recipe Engine to allow load-shed commands to override recipe setpoints without modifying the recipe state machine. | architecture-decisions | Architecture Decisions |  | Inspection | 43 |  | Separation of Emergency Shutdown Sequencer preserves shutdown capability during network failures. Crop Recipe Engine decoupled from Plant Management Server allows recipe execution to survive server updates. DR Handler separation prevents demand-response events from corrupting crop recipe state. | architecture, supervisory-control, session-469, idempotency:arc-supervisory-control-469
ARC-REQ-010 | ARC: Zone Controller Network — distributed embedded controllers with OPC-UA aggregation gateway. Zone Controller Units are selected as standalone embedded Linux nodes (not PLCs) to enable recipe-driven Python control loops without proprietary programming environments; the Edge Gateway pattern decouples the OPC-UA server from per-zone hardware, allowing supervisory software upgrades without touching field devices. Industrial Ethernet with VLAN segregation was chosen over a dedicated fieldbus (PROFIBUS, CANopen) to leverage standard IT network management tooling and support future bandwidth growth for video-based crop monitoring. | architecture-decisions | Architecture Decisions |  | Analysis | 57 |  | Architecture decision for Zone Controller Network subsystem: embedded Linux ZCU nodes selected over PLCs for recipe-driven Python control; Edge Gateway decouples OPC-UA server from field hardware; industrial Ethernet with VLAN segregation preferred over fieldbus for standard IT tooling and future bandwidth growth. | architecture, zone-controller-network, session-470, idempotency:arc-zone-controller-network-470
ARC-REQ-011 | ARC: Data Acquisition and Compliance Subsystem — TSDB-centred data store with separate recipe database and automated report generation. A time-series database (InfluxDB) was selected over a relational database for environmental telemetry because sensor data ingestion at 1Hz per channel per zone produces high-cardinality sequential writes that relational engines handle poorly at 10-year retention scale. The recipe and compliance subsystems use a relational database (PostgreSQL) because their data is structured, low-volume, and requires referential integrity for audit chains. The OpenADR VEN is deployed as a co-located service to share the TSDB's energy telemetry without requiring a separate data bus. | architecture-decisions | Architecture Decisions |  | Analysis | 57 |  | Architecture decision for Data Acquisition and Compliance Subsystem: InfluxDB selected for high-cardinality sequential sensor writes; PostgreSQL for recipe and compliance data requiring referential integrity; OpenADR VEN co-located with TSDB to share energy telemetry without additional data bus. | architecture, data-acquisition, session-470, idempotency:arc-data-acquisition-470
IFC-REQ-001 | The interface between the Vertical Farm Environment Controller and the Building Management System SHALL use BACnet/IP with event-driven alarm exchange (fire alarm status within 500ms) and 5-minute polled energy consumption metrics, supporting BACnet Alarm and Event services (clause 13) and Read Property services. | interface-requirements | Interface Requirements |  | Test | 86 |  | External interface: BMS provides fire alarm status that feeds safety interlock chain and weather data for HVAC anticipatory control. 500ms alarm latency ensures fire alarm reaches safety interlock subsystem before flashover conditions develop in adjacent building spaces. | interface, external, session-462, idempotency:ifc-ext-bms-462
IFC-REQ-002 | The interface between the Vertical Farm Environment Controller and the Crop Planning/ERP Software SHALL use REST API (JSON over HTTPS) with mutual TLS authentication, supporting crop recipe download, zone scheduling commands, and environmental log/harvest data upload with maximum API response time of 5 seconds. | interface-requirements | Interface Requirements |  | Test | 86 |  | External interface: ERP provides crop recipes that drive zone setpoints and schedules. Mutual TLS prevents recipe tampering (wrong recipe loaded is a ConOps failure mode). 5-second API timeout prevents cloud latency from blocking operational control loops. | interface, external, session-462, idempotency:ifc-ext-erp-462
IFC-REQ-003 | The interface between the Vertical Farm Environment Controller and the Energy Management/Smart Grid SHALL support OpenADR 2.0b VEN profile for demand-response signal reception and Modbus TCP (Function Code 3/4) for local energy metering at 15-second scan rate, with DR event acknowledgement within 60 seconds. | interface-requirements | Interface Requirements |  | Test | 86 |  | External interface: Utility sends DR signals that trigger load curtailment. OpenADR 2.0b VEN profile is the standard for demand-response loads >100kW. 15-second Modbus metering provides granularity for real-time load tracking used by the energy optimisation function. | interface, external, session-462, idempotency:ifc-ext-grid-462
IFC-REQ-004 | The interface between the Vertical Farm Environment Controller and the Cloud Monitoring Platform SHALL use MQTT v5 over TLS 1.3 for 1-minute telemetry push (all zone sensors, actuator states, active alarms) and configuration update pull, with automatic local-only fallback within 30 seconds of connectivity loss and data backfill upon reconnection. | interface-requirements | Interface Requirements |  | Test | 86 |  | External interface: Cloud platform provides analytics, anomaly detection, and remote monitoring. MQTT v5 session expiry and message retention support reconnection backfill. 30-second fallback ensures control loops are not affected by internet outages. | interface, external, session-462, idempotency:ifc-ext-cloud-462
IFC-REQ-005 | The interface between the Vertical Farm Environment Controller and the CO2 Bulk Supply System SHALL use 4-20mA analogue inputs for tank level (0-100%) and tank pressure (0-25 bar), and 24VDC digital outputs for zone CO2 solenoid valves (fail-closed on loss of signal), with the controller monitoring tank level for automatic reorder trigger at 20% remaining. | interface-requirements | Interface Requirements |  | Test | 86 |  | External interface: CO2 supply system is safety-critical — regulator failure drives H-001 asphyxiation hazard. 4-20mA is industry standard for hazardous area analogue instruments. Fail-closed solenoid on loss of signal ensures CO2 injection stops on any communication or power failure. | interface, external, safety, session-462, idempotency:ifc-ext-co2-supply-462
IFC-REQ-006 | The interface between the CO2 Safety Sensor Array and the Safety PLC SHALL use hardwired 4–20mA analog signals (one per sensor channel), with channel-open and channel-short detection, at a scan rate of ≤1s per channel, providing CO2 concentration readings in the range 0–10,000 ppm. | interface-requirements | Interface Requirements |  | Test | 86 |  | A hardwired 4-20mA interface is intrinsically fail-safe: a broken wire drives the current to 0mA (below the 4mA live-zero), which the Safety PLC detects as a fault rather than a valid zero-CO2 reading. This prevents a wiring fault from masking a CO2 hazard. Digital fieldbus alternatives are excluded because they could be compromised by a network fault or cyber event at precisely the moment CO2 is rising. | interface, safety-interlock, sil-3, session-463, idempotency:ifc-co2-sensor-plc-463
IFC-REQ-007 | The interface between the Safety PLC and the Hardwired Trip Bus SHALL consist of 24VDC relay coil outputs (energize-to-hold topology), with each output driving a safety relay module that controls one final element; wire-break detection SHALL be active on all relay coil circuits. | interface-requirements | Interface Requirements |  | Inspection | 86 |  | Energize-to-hold (de-energize-to-trip) ensures that any relay coil circuit failure — broken wire, power loss, PLC output card failure — results in the relay de-energising and the final element moving to the safe state. This is the foundation of the fail-safe architecture required by IEC 61511 for SIL 3 final elements. Wire-break detection catches open circuits before they become undetected latent faults. | rt-vague-interface, red-team-session-480
IFC-REQ-008 | The interface between the Lockout Tagout Controller and the Safety PLC SHALL provide a hardwired zone-inhibit signal (24VDC discrete, normally-open) for each zone; when a LOTO key is checked out, the signal SHALL be de-asserted, preventing Safety PLC from enabling any output in that zone. | interface-requirements | Interface Requirements |  | Demonstration | 86 |  | OSHA 29 CFR 1910.147 requires energy isolation. Implementing LOTO as a hardwired inhibit to the Safety PLC ensures that software running on the supervisory layer cannot override LOTO state. The de-asserted signal (open circuit) maps to inhibit, so a broken LOTO wire conservatively defaults to inhibited — preventing inadvertent re-energisation while fault is investigated. | rt-vague-interface, red-team-session-480
IFC-REQ-009 | The interface between the Supervisory Control Subsystem and the Zone Controller Network SHALL use Modbus TCP/IP or OPC UA to distribute crop recipe parameters and zone setpoints with latency not exceeding 500ms per zone update. | interface-requirements | Interface Requirements | ubiquitous | Test | 100 |  | STK-REQ-002 requires setpoint propagation within 60 seconds. The 500ms per-zone latency ensures that for up to 100 zones, all zones receive updated recipe parameters within the 60-second window. Modbus TCP/IP and OPC UA are the de facto standards for industrial HVAC and process control integration. | idempotency:ifc-sc-zcn-recipe-464b
IFC-REQ-010 | The interface between the CO2 Enrichment Subsystem and the Zone Controller Network SHALL exchange CO2 concentration measurements at 1Hz per zone via Modbus TCP/IP, with each zone's current ppm reading and valve position feedback available to the supervisory layer within 2 seconds. | interface-requirements | Interface Requirements | ubiquitous | Test | 86 |  | SYS-REQ-003 requires CO2 regulation within ±50 ppm. 1Hz feedback matches the sensor reporting rate and allows the supervisory layer to detect concentration drift and adjust injection in time to maintain the ±50 ppm band. The 2-second delivery window provides headroom for Modbus TCP poll cycles on a 100-zone network. | idempotency:ifc-co2-zcn-feedback-464
IFC-REQ-011 | The interface between the Climate Management Subsystem and the Zone Controller Network SHALL provide per-zone HVAC actuator commands (damper position 0-100%, compressor enable/disable, fan speed setpoint) with command execution acknowledgement within 1 second. | interface-requirements | Interface Requirements | ubiquitous | Test | 100 |  | SYS-REQ-001 (temperature ±1°C) and SYS-REQ-002 (humidity ±5% RH) require closed-loop HVAC control. The 1-second acknowledgement window allows the Climate Management Subsystem to detect actuator faults and invoke the SYS-REQ-008 degraded-mode response before zone temperature deviates beyond 2°C. | rt-vague-interface, red-team-session-480
IFC-REQ-012 | The interface between the Nutrient Management Subsystem and the Zone Controller Network SHALL relay zone-level dosing commands (acid/base pump enable, irrigation valve open/close, flow rate setpoint) via Modbus TCP/IP and SHALL report per-zone EC and pH measurements at 0.1Hz with accuracy of ±0.1 mS/cm EC and ±0.05 pH. | interface-requirements | Interface Requirements | ubiquitous | Test | 86 |  | SYS-REQ-006 requires pH regulation within ±0.2. Zone-level feedback accuracy of ±0.05 pH must be tighter than the system-level tolerance to accommodate sensor aging and calibration drift. Irrigation valve state reporting is needed to detect the stuck-open condition in SYS-REQ-010. | idempotency:ifc-nm-zcn-nutrient-464
IFC-REQ-013 | The interface between the Horticultural Lighting Subsystem and the Zone Controller Network SHALL distribute per-zone LED intensity and spectrum commands (PWM duty cycle 0-100% per channel) via DALI-2 or DMX512 protocol with LED fixture surface temperature telemetry returned at 0.2Hz. | interface-requirements | Interface Requirements | ubiquitous | Test | 86 |  | SYS-REQ-005 requires LED intensity within ±5% of recipe setpoints. DALI-2 is IEC 62386-certified for digital LED control with per-fixture dimming accuracy of ±1%. Surface temperature telemetry at 0.2Hz satisfies SYS-REQ-009, which requires trip response within 10 seconds of exceeding 85°C. | idempotency:ifc-hl-zcn-lighting-464
IFC-REQ-014 | The interface between the Safety Interlock Subsystem and the CO2 Enrichment Subsystem SHALL consist of a hardwired de-energize-to-trip 24VDC relay signal that forces the CO2 bulk supply solenoid valve to the closed state within 500ms of an interlock trip, independent of any software controller. | interface-requirements | Interface Requirements | ubiquitous | Inspection | 86 |  | SYS-REQ-004 requires CO2 shutoff within 10 seconds of the 5000 ppm threshold. A hardwired relay directly controlling the supply solenoid is the only architecture guaranteeing trip times independent of network latency or software availability. The 500ms margin leaves 9.5 seconds for actuator stroke time. | idempotency:ifc-sis-co2-trip-464
IFC-REQ-015 | The interface between the Safety Interlock Subsystem and the Supervisory Control Subsystem SHALL provide a unidirectional read-only OPC UA status bus reporting interlock state, trip cause code, and last-trip timestamp with polling interval not exceeding 1 second. | interface-requirements | Interface Requirements | ubiquitous | Test | 86 |  | STK-REQ-001 requires HMI display of zone status and SYS-REQ-011 requires audit logging. The Supervisory Control Subsystem must not be able to acknowledge or reset trips via software to preserve SIL 3 integrity. A unidirectional OPC UA server/client topology enforces isolation while enabling state visibility. | idempotency:ifc-sis-sc-status-464
IFC-REQ-016 | The interface between the Data Acquisition and Compliance Subsystem and the Zone Controller Network SHALL collect 1-minute-resolution readings of all environmental parameters (temperature, humidity, CO2, PAR, EC, pH, irrigation flow) from each zone controller via OPC UA subscription, timestamped to UTC ±1 second accuracy. | interface-requirements | Interface Requirements | ubiquitous | Test | 86 |  | STK-REQ-005 requires data retention compliant with food safety reference standards. 1-minute resolution is the minimum for post-harvest environmental correlation required by FSMA traceability frameworks. UTC ±1 second synchronisation is needed for multi-zone event correlation in compliance audits. | idempotency:ifc-dac-zcn-logging-464
IFC-REQ-017 | The interface between the Supervisory Control Subsystem and the Data Acquisition and Compliance Subsystem SHALL allow on-demand compliance report generation via REST API, returning the complete dataset within 5 minutes for any date range up to 90 days. | interface-requirements | Interface Requirements | ubiquitous | Test | 86 |  | STK-REQ-012 requires energy-use reporting and STK-REQ-005 requires compliance data access. A REST API allows the HMI and cloud platform to pull historical datasets without direct database access, isolating the compliance data store from operational control traffic. | idempotency:ifc-sc-dac-reports-464
IFC-REQ-018 | The interface between the Climate Management Subsystem and the Safety Interlock Subsystem SHALL provide a hardwired zone-temperature out-of-range contact closure (24VDC) to the Safety PLC input card when any zone exceeds 38°C, with signal propagation time not exceeding 100ms. | interface-requirements | Interface Requirements | ubiquitous | Test | 86 |  | SYS-REQ-009 requires trip of LED fixtures when zone temperature exceeds 38°C. A hardwired input to the Safety PLC ensures the thermal trip condition is evaluated by the SIL 3 Voted Logic Engine independently of process network health. The 100ms propagation budget fits within the 10-second trip response window in SYS-REQ-009. | idempotency:ifc-cm-sis-thermal-464
IFC-REQ-019 | The interface between the Nutrient Management Subsystem and the Safety Interlock Subsystem SHALL provide a hardwired dosing-excess fault contact closure (24VDC) to the Safety PLC input card when cumulative acid/base injection exceeds 5% of tank volume within any 10-minute window, with signal propagation time not exceeding 200ms. | interface-requirements | Interface Requirements | ubiquitous | Test | 86 |  | SYS-REQ-007 defines the pH dosing excess condition as a safety trip requiring valve closure within 5 seconds. A hardwired signal path ensures the dosing-excess condition feeds directly into the SIL 3 Voted Logic Engine without relying on Modbus network availability, satisfying the independence requirement of SYS-REQ-015. | idempotency:ifc-nm-sis-dosing-464
IFC-REQ-020 | The interface between the Supervisory Control Subsystem and the CO2 Enrichment Subsystem SHALL provide zone-level CO2 concentration setpoints (400-2000 ppm range, ±1 ppm resolution) and injection enable/disable commands via Modbus TCP/IP with command acknowledgement within 2 seconds. | interface-requirements | Interface Requirements | ubiquitous | Test | 86 |  | SYS-REQ-003 requires CO2 regulation within ±50 ppm of crop recipe setpoints. The Supervisory Control Subsystem holds the crop recipe (STK-REQ-002) and must transmit updated CO2 setpoints to the CO2 Enrichment Subsystem. The 400-2000 ppm range covers ambient to the maximum enrichment for fruiting crops. | idempotency:ifc-sc-co2-setpoint-464
IFC-REQ-021 | The interface between the Zone Controller Network and the Supervisory Control Subsystem SHALL publish zone fault events (sensor out-of-range, actuator fault, communication timeout) as OPC UA events with severity classification and zone identifier, delivered within 3 seconds of fault detection. | interface-requirements | Interface Requirements | ubiquitous | Test | 86 |  | STK-REQ-003 requires crop yield impact assessment within 10 minutes of environmental excursions. STK-REQ-001 requires HMI status display with 5-second update latency. The 3-second event delivery window provides the required headroom for HMI rendering while giving the supervisory layer time to initiate yield impact calculations. | idempotency:ifc-zcn-sc-faults-464
IFC-REQ-022 | The interface between the CO2 Injection Controller and the Zone NDIR CO2 Sensor Array SHALL use 4-20mA analogue signals (one per zone), corresponding to 300–3000 ppm full-scale, with the CO2 Injection Controller detecting sensor fault conditions (open circuit <3.6mA, saturation >20.5mA) and raising a zone fault alarm within 5 seconds. | interface-requirements | Interface Requirements |  | Test | 86 |  | 4-20mA is the industry standard for process sensor interfaces due to its noise immunity in electrically noisy grow-room environments (motor drives, lighting ballasts). The live-zero (4mA) enables open-circuit fault detection, which is essential for a process control loop — loss of feedback must be detectable. | interface, co2-enrichment-subsystem, session-465, idempotency:ifc-ctrl-ndir-465
IFC-REQ-023 | The interface between the CO2 Injection Controller and the Zone Solenoid Valve Array SHALL use 24VDC discrete output signals (one per zone) energise-to-open, with valve position feedback returned as 24VDC discrete input (one per zone), and the CO2 Injection Controller SHALL detect valve-open command-feedback discrepancy within 2 seconds and raise a valve fault alarm. | interface-requirements | Interface Requirements |  | Test | 86 |  | 24VDC discrete I/O is the standard interface for solenoid valve control, providing clean on/off switching without analogue noise concerns. Position feedback detection of command/state discrepancy within 2s is required to detect valve seizure or coil failure before it causes out-of-specification CO2 enrichment or dangerous valve-open-on-trip conditions. | rt-vague-interface, red-team-session-480
IFC-REQ-024 | The interface between the CO2 Distribution Manifold and the CO2 Injection Controller SHALL transmit manifold inlet pressure (0–10 bar, 4-20mA) and manifold temperature (−10 to 40°C, 4-20mA) to the CO2 Injection Controller at 1Hz, with the controller raising a low-pressure alarm at <1.3 bar and shutting all zone valves at <0.5 bar to prevent CO2 reverse-flow. | interface-requirements | Interface Requirements |  | Test | 86 |  | Manifold pressure monitoring is needed to detect bulk CO2 supply exhaustion and vaporiser faults before they cause control failures. 1.3 bar low-pressure alarm gives operators time to top up supply before injection is lost; 0.5 bar shutdown prevents CO2 reverse-flow through valves, which could damage equipment and corrupt sensor readings. | interface, co2-enrichment-subsystem, session-465, idempotency:ifc-manifold-ctrl-465
IFC-REQ-025 | The interface between the EC/pH Sensor Array and the Irrigation Controller SHALL transmit EC (mS/cm) and pH measurements per zone via Modbus RTU RS-485 at 9600 baud with 16-bit register encoding, including a fault status register, at a polling rate of 0.1 Hz per zone, with maximum measurement-to-register latency of 500 ms. | interface-requirements | Interface Requirements |  | Test | 86 |  | Modbus RTU RS-485 is selected over 4-20mA because it allows single-cable multi-drop wiring across all zones, simplifying installation in large vertical farms with many grow zones. A fault status register is mandatory to support SUB-REQ-025 (fault detection) — analogue 4-20mA cannot carry fault state without a separate discrete signal. The 0.1Hz polling rate matches the measurement rate and ensures dosing corrections respond to the most current reading without excessive bus load. | interface, nutrient-management-subsystem, session-466, idempotency:ifc-ecph-ic-466
IFC-REQ-026 | The interface between the Irrigation Controller and the Dosing Pump Array SHALL transmit pump enable commands (per pump: on/off, target volume in mL) via Modbus TCP at 100 Mbit/s, with command round-trip confirmation within 1 second, and SHALL receive cumulative injection counters (per pump, in mL) for watchdog monitoring at 1 Hz. | interface-requirements | Interface Requirements |  | Test | 86 |  | Modbus TCP is used (over Modbus RTU) for the Irrigation Controller to Dosing Pump Array interface because the Irrigation Controller already uses Ethernet for Zone Controller Network communication (IFC-REQ-012), and maintaining a single network avoids separate RS-485 field cabling to the pump cabinet. Cumulative injection counters are returned at 1Hz to enable the Irrigation Controller to mirror the watchdog counter state for alarming before the hardwired SIL-2 trip is reached. | interface, nutrient-management-subsystem, session-466, idempotency:ifc-ic-dpa-466
IFC-REQ-027 | The interface between the Irrigation Controller and the Zone Irrigation Valve Array SHALL use 24VAC energise-to-open discrete outputs, one per zone valve, with Irrigation Controller reading reed-switch position feedback (24VDC open-collector, one per valve) within 2 seconds of each commanded state change; any position confirmation timeout SHALL be reported as a stuck-valve fault to the Zone Controller Network. | interface-requirements | Interface Requirements |  | Test | 86 |  | 24VAC discrete control is standard for solenoid valve actuation in hydroponic systems, providing galvanic isolation between control and power circuits and compatibility with off-the-shelf irrigation valve hardware. Position feedback integration at the Irrigation Controller (rather than at the Zone Controller Network) localises the stuck-valve detection logic (SUB-REQ-030) to the component responsible for valve commands, enabling sub-30-second detection without polling latency through a higher-level network. | rt-vague-interface, red-team-session-480
IFC-REQ-028 | The interface between the Recirculation Pump System and the Nutrient Reservoir and Mixing System SHALL consist of a DN50 suction connection from the reservoir outlet to the pump inlet, with a float-type dry-run protection switch on the reservoir monitoring fluid level at the pump inlet centerline, transmitting a 24VDC discrete signal to the pump VFD safety input; loss of the signal SHALL inhibit pump start. | interface-requirements | Interface Requirements |  | Inspection | 86 |  | A physical float switch on the reservoir at pump inlet centerline provides faster dry-run detection than an ultrasonic level sensor alarm threshold (SUB-REQ-036 low-level alarm is at 20% capacity, which may still leave fluid above the inlet). The hardwired 24VDC signal to the VFD safety input ensures dry-run inhibit is enforced even if the Irrigation Controller communication is lost, preventing pump damage independent of software. | rt-vague-interface, red-team-session-480
IFC-REQ-029 | The interface between the Lighting Control Unit and the LED Driver Module Array SHALL use DALI-2 (IEC 62386 Part 209) at 1200 baud, supporting per-channel dimming commands with 16-bit address and 8-bit level resolution, and SHALL receive driver status responses including fault codes within 22 ms. | interface-requirements | Interface Requirements |  | Test | 86 |  | DALI-2 is selected over 0-10V analog for its bidirectional fault reporting capability — essential in a 400kW+ facility where silent driver failure would degrade PAR accuracy without indication. 22ms response time derives from DALI-2 bus timing specification and allows within-scan fault detection at the LCU 100ms control cycle. | interface, horticultural-lighting, session-467, idempotency:ifc-lcu-driverarray-dali-467
IFC-REQ-030 | The interface between the PAR Sensor Array and the Lighting Control Unit SHALL transmit calibrated PPFD measurements in the range 0-2000 µmol/m²/s at a minimum rate of 1 Hz via 4-20 mA analog loop or RS-485 Modbus RTU, with loss-of-signal detection within 3 seconds. | interface-requirements | Interface Requirements |  | Test | 86 |  | 1 Hz sampling matches the LCU PAR PID control cycle and provides sufficient response bandwidth for closed-loop regulation. 3-second loss-of-signal detection is required to trigger the degraded-mode fallback (SUB-REQ-046) promptly enough to avoid a control gap exceeding one photoperiod scheduling step. | interface, horticultural-lighting, session-467, idempotency:ifc-par-lcu-measurement-467
IFC-REQ-031 | The interface between the Fixture Thermal Monitoring Array and the Safety Interlock Subsystem SHALL be a normally-closed 24 V DC hardwired signal on the trip bus: signal opens when any fixture heatsink exceeds 85 degrees C, using a dedicated comparator circuit with no programmable components in the trip path. | interface-requirements | Interface Requirements |  | Test | 86 |  | SIL 2 classification of the thermal trip function (SUB-REQ-042) requires that no software is in the trip path per IEC 61508 clause 7.4.2.3. Normally-closed configuration ensures that wiring faults (open circuit, short to ground) result in a spurious trip rather than a missed trip, which is the correct safe-fail direction for a fire-prevention function. | interface, horticultural-lighting, sil-2, session-467, idempotency:ifc-thermal-safetyinterlock-hardwired-467
IFC-REQ-032 | The interface between the Temperature Sensor Network and the Zone Climate Controller SHALL transmit 16-bit RTD resistance readings for all zone sensors at 1 Hz via 4-wire PT100 multiplexer bus, with bus fault detection (open-circuit and short-circuit conditions) reported within 1 measurement cycle. | interface-requirements | Interface Requirements |  | Test | 86 |  | 1 Hz transmission matches the PID sampling period; 16-bit resolution provides 0.01 degC step size sufficient for ±1.0 degC zone control. Bus fault detection in one cycle (1 s) ensures sensor loss is detected before the next PID iteration could produce a runaway output. | interface, climate-management, session-469, idempotency:ifc-tsn-zcc-469
IFC-REQ-033 | The interface between the Zone Climate Controller and the HVAC Actuator Interface SHALL use Modbus RTU over RS-485 at 19200 baud, with the Zone Climate Controller as master issuing setpoint write registers and reading status registers at 2 Hz, and the HVAC Actuator Interface responding within 100 ms per Modbus specification. | interface-requirements | Interface Requirements |  | Test | 86 |  | Modbus RTU at 19200 baud is the established HVAC industry standard for this scale of installation, supported by all candidate VFD and actuator vendors. 2 Hz polling is sufficient to detect actuator faults within the 1 s confirmation latency in SUB-REQ-059 while keeping bus utilisation below 20 percent. | interface, climate-management, session-469, idempotency:ifc-zcc-hvac-actuator-469
IFC-REQ-034 | The interface between the Fresh Air Ventilation Controller and the CO2 Enrichment Subsystem SHALL use Modbus TCP over Ethernet at 100 Mbit/s, exchanging zone CO2 concentration (ppm, 16-bit) and fresh-air fraction setpoint (percent, 8-bit) at 0.5 Hz with a maximum round-trip latency of 200 ms. | interface-requirements | Interface Requirements |  | Test | 86 |  | Modbus TCP reuses the existing plant Ethernet network already used by the CO2 subsystem, avoiding a separate serial bus. 0.5 Hz exchange rate is sufficient for fresh-air fraction coordination since the HRV damper actuator response time is 10-20 s. The 200 ms latency bound is 10x less than the HRV actuator response time, ensuring coordination data does not become stale. | interface, climate-management, session-469, idempotency:ifc-favc-co2-469
IFC-REQ-035 | The interface between the Crop Recipe Engine and the environmental subsystems (Climate Management, Lighting, Nutrient, CO2 Enrichment) SHALL use OPC-UA over Ethernet at 1 Gbit/s, with setpoint publish intervals of 60 s during steady-state recipe execution and 5 s during rapid-ramp recipe transitions, with a maximum delivery latency of 500 ms per setpoint write. | interface-requirements | Interface Requirements |  | Test | 86 |  | OPC-UA provides a vendor-neutral, standardised SCADA interface supported by all major PLC and controller vendors. 60 s normal publish interval matches the slowest setpoint change rate in any registered crop recipe; 5 s rapid-ramp interval is needed for lighting pre-dawn simulation ramps. 500 ms delivery latency is 10x less than any subsystem's actuator response time. | interface, supervisory-control, session-469, idempotency:ifc-cre-subsystems-469
IFC-REQ-036 | The interface between the Emergency Shutdown Sequencer and the Safety Interlock Subsystem SHALL use a hardwired 24V DC discrete signal bus with dedicated signal lines for each shutdown phase (CO2 valve trip, nutrient pump stop, lighting kill, HVAC purge), with signal propagation latency not exceeding 20 ms end-to-end. | interface-requirements | Interface Requirements |  | Test | 86 |  | Hardwired interface is mandatory for safety-critical shutdown paths per IEC 61511. Network-based commands are insufficient for CO2 and thermal hazard mitigation because network failure must not prevent emergency shutdown. 20 ms propagation latency is negligible relative to the 10 s total sequence time budget. | interface, supervisory-control, session-469, idempotency:ifc-ess-safety-interlock-469
IFC-REQ-037 | The interface between the Zone Controller Unit and the Zone Edge Gateway SHALL use OPC-UA over 100Mbps Ethernet with security mode SignAndEncrypt (Basic256Sha256 security policy), transferring zone telemetry and setpoint commands at a publish interval of 100 ms and a maximum message size of 4096 bytes. | interface-requirements | Interface Requirements |  | Test | 86 |  | OPC-UA is the standard industrial interoperability protocol for this application; SignAndEncrypt prevents man-in-the-middle attacks on control commands. 100ms publish interval meets the 500ms end-to-end latency budget (SUB-REQ-069). 4096-byte message limit is sized for 24 data nodes (12 parameters × 2 zones per controller) with OPC-UA encoding overhead. | interface, zone-controller-network, session-470, idempotency:ifc-zcn-zcu-gateway-opcua-470
IFC-REQ-038 | The interface between the Zone Controller Unit and Zone I/O Expansion Module SHALL use RS-485 Modbus RTU at 115200 baud, with the ZCU as master polling all connected I/O modules at a cycle time not exceeding 250 ms per scan across up to 4 modules on a single RS-485 segment. | interface-requirements | Interface Requirements |  | Test | 86 |  | RS-485 Modbus RTU provides electrically isolated, deterministic field bus communications suitable for the wet, chemical-laden growing zone environment. 115200 baud and 250ms scan time ensures analog samples reach the ZCU PID loop within the 10 Hz control cycle. Supporting up to 4 modules per segment covers the maximum I/O count for a single zone without additional repeaters. | interface, zone-controller-network, session-470, idempotency:ifc-zcn-zcu-iom-rs485-470
IFC-REQ-039 | The interface between the Industrial Ethernet Switch and all connected OT devices SHALL enforce IEEE 802.1Q VLAN segmentation such that zone-controller operational traffic (VLAN 100) is physically isolated at Layer 2 from safety-interlock traffic (VLAN 200), with zero cross-VLAN unicast forwarding permitted without explicit inter-VLAN routing policy. | interface-requirements | Interface Requirements |  | Inspection | 86 |  | SYS-REQ-015 requires SIL-3 independence for safety-critical functions; VLAN segregation at the switch layer prevents broadcast storms or misconfigured zone controller software from disrupting the Safety Interlock Subsystem network. Inspection verification via switch configuration audit is more reliable than runtime test for negative-traffic requirements. | interface, zone-controller-network, session-470, idempotency:ifc-zcn-switch-vlan-470
IFC-REQ-040 | The interface between the Zone Edge Gateway and the Time-Series Database Engine SHALL use MQTT over TLS 1.2 (topic: farm/<zone-id>/<parameter>/raw, QoS level 1) for real-time sensor data ingestion at 1Hz per channel, with the TSDB MQTT broker acknowledging each message within 500 ms and persisting data within 2 seconds of receipt. | interface-requirements | Interface Requirements |  | Test | 86 |  | MQTT QoS 1 guarantees at-least-once delivery without the head-of-line blocking that QoS 2 introduces, which is appropriate for sensor telemetry where duplicate samples are preferable to data gaps. TLS 1.2 protects OT network data from eavesdropping. The 2-second persistence deadline ensures data is written to durable storage before any TSDB process failure could cause loss. | interface, data-acquisition, session-470, idempotency:ifc-dac-gateway-tsdb-mqtt-470
IFC-REQ-041 | The interface between the Supervisory Control Subsystem and the Crop Recipe Database SHALL use a REST API over HTTPS (TLS 1.2, mutual authentication with X.509 client certificates), with recipe read operations responding within 500 ms and recipe write operations (create/update) completing within 2 seconds under a load of 10 concurrent requests. | interface-requirements | Interface Requirements |  | Test | 86 |  | The Supervisory HMI must load and switch crop recipes during active growth operations; the 500ms read latency ensures operator-initiated recipe activation does not disrupt crop monitoring workflows. Mutual TLS authentication prevents unauthorised recipe modification from misconfigured HMI client software. | interface, data-acquisition, session-470, idempotency:ifc-dac-supervisory-recipedb-470
IFC-REQ-042 | The interface between the OpenADR Virtual End Node and the Supervisory Control Subsystem SHALL use an internal message queue (AMQP or equivalent) with message routing key 'dr.event.curtailment', carrying structured curtailment payloads (JSON: event_id, start_time, duration_s, load_reduction_kw, affected_zones[]) with end-to-end delivery latency not exceeding 5 seconds. | interface-requirements | Interface Requirements |  | Test | 86 |  | Internal message queue decouples the OpenADR VEN (utility-protocol-facing) from the Supervisory (farm-protocol-facing), allowing each to evolve independently and preventing a utility communication fault from blocking supervisory operations. 5s delivery is derived from the 30s acknowledgement window minus 25s buffer for Supervisory pre-conditioning. | rt-vague-interface, red-team-session-480
STK-REQ-001 | The Vertical Farm Environment Controller SHALL provide zone-specific environmental dashboards displaying real-time temperature, humidity, CO2, PAR level, and nutrient status with update latency not exceeding 5 seconds. | stakeholder-requirements | Stakeholder Requirements |  | Demonstration | 100 |  | Grower Technician, Daily Growing Cycle: Technician reviews dashboard at shift start to assess zone status and identify deviations requiring manual intervention. 5-second latency ensures displayed values reflect current conditions during walkthrough inspections. | stakeholder, stk-grower, session-462, idempotency:stk-grower-dashboard-462
STK-REQ-002 | The Vertical Farm Environment Controller SHALL allow grower technicians to modify zone-specific crop recipe parameters (PAR intensity, photoperiod timing, temperature setpoints, nutrient EC/pH targets) from the HMI with changes taking effect within 60 seconds. | stakeholder-requirements | Stakeholder Requirements |  | Test | 100 |  | Grower Technician, Daily Growing Cycle: Technician adjusts Zone 5 lettuce PAR based on growth analytics. Recipe modifications must propagate quickly to zone controllers so the technician can verify the effect during the same visit. | stakeholder, stk-grower, session-462, idempotency:stk-grower-recipe-462
STK-REQ-003 | The Vertical Farm Environment Controller SHALL provide the facility manager with estimated crop yield impact within 10 minutes of any environmental excursion exceeding zone setpoint tolerances. | stakeholder-requirements | Stakeholder Requirements |  | Test | 100 |  | Facility Manager, HVAC Failure: Manager needs to assess production impact of thermal excursions to make degraded-mode operational decisions (e.g., accept reduced yield vs. emergency HVAC procurement). | stakeholder, stk-manager, session-462, idempotency:stk-manager-yield-impact-462
STK-REQ-004 | The Vertical Farm Environment Controller SHALL enable the facility manager to schedule maintenance windows per zone without disrupting active crop cycles in adjacent zones. | stakeholder-requirements | Stakeholder Requirements |  | Demonstration | 100 |  | Facility Manager, Crop Changeover: Production scheduling requires per-zone maintenance windows that do not cascade environmental disturbances to neighbouring zones through shared HVAC or nutrient systems. | stakeholder, stk-manager, session-462, idempotency:stk-manager-scheduling-462
STK-REQ-005 | The Vertical Farm Environment Controller SHALL support sensor calibration routines with guided procedures, automatic logging of calibration events, and comparison against reference standards for the maintenance technician. | stakeholder-requirements | Stakeholder Requirements |  | Demonstration | 100 |  | Maintenance Technician, Sensor Drift: pH sensor drift scenario demonstrates that routine calibration is essential. Guided procedures with reference comparison reduce calibration errors. Automatic logging creates maintenance audit trail required by food safety standards. | stakeholder, stk-maintenance, session-462, idempotency:stk-maint-calibration-462
STK-REQ-006 | The Vertical Farm Environment Controller SHALL provide maintenance lockout/tagout capability per zone, preventing automatic actuator operation in isolated zones while allowing adjacent zones to continue automated operation. | stakeholder-requirements | Stakeholder Requirements |  | Test | 100 |  | Maintenance Technician, Maintenance mode: Technician must safely access zone equipment (LEDs, pumps, HVAC components) without risk of automatic actuator activation. Zone isolation must not compromise adjacent zone control. | stakeholder, stk-maintenance, session-462, idempotency:stk-maint-lockout-462
STK-REQ-007 | The Vertical Farm Environment Controller SHALL maintain zone CO2 concentration below 5000 ppm TWA and temperature below 35°C whenever harvest crew personnel are present in a growing zone. | stakeholder-requirements | Stakeholder Requirements |  | Test | 100 |  | Harvest Crew Worker, Crop Changeover and CO2 Emergency: Non-technical harvest crew cannot be expected to monitor environmental conditions. Controller must guarantee safe atmospheric conditions during occupied periods. 5000ppm is OSHA TWA limit; 35°C is heat stress threshold for moderate physical work. | stakeholder, stk-harvest-crew, session-462, idempotency:stk-harvest-safety-462
STK-REQ-008 | The Vertical Farm Environment Controller SHALL switch zones to worker-comfort mode (22°C, 50% white light, CO2 enrichment off) when harvest crew zone entry is confirmed, and prevent return to production mode until crew exit is confirmed. | stakeholder-requirements | Stakeholder Requirements |  | Demonstration | 86 |  | Harvest Crew Worker, Crop Changeover: Harvest crew enters Zone 1 for lettuce harvest — controller transitions to comfortable working conditions. Two-state interlock (entry/exit confirmed) prevents premature return to production conditions with high CO2 or extreme lighting. | stakeholder, stk-harvest-crew, session-462, idempotency:stk-harvest-comfort-462
STK-REQ-009 | The Vertical Farm Environment Controller SHALL maintain tamper-evident, time-stamped environmental data logs with minimum 2-year retention covering temperature, humidity, CO2, pH, EC, and irrigation events for all zones, accessible for food safety audit within 4 hours of request. | stakeholder-requirements | Stakeholder Requirements |  | Inspection | 86 |  | Food Safety Auditor: BRCGS/SQF certification requires demonstrated environmental control with auditable records. HACCP principles demand continuous monitoring logs. 2-year retention covers multiple audit cycles. 4-hour retrieval supports audit day workflow. | stakeholder, stk-auditor, session-462, idempotency:stk-auditor-logs-462
STK-REQ-010 | The Vertical Farm Environment Controller SHALL generate HACCP-compliant deviation reports identifying any period where environmental parameters exceeded food-safety-critical thresholds, including corrective actions taken. | stakeholder-requirements | Stakeholder Requirements |  | Inspection | 100 |  | Food Safety Auditor: Auditors require documentation of deviations and corrective actions per HACCP Principle 5. Automated report generation ensures consistent documentation and reduces audit preparation workload. | stakeholder, stk-auditor, session-462, idempotency:stk-auditor-haccp-462
STK-REQ-011 | The Vertical Farm Environment Controller SHALL respond to OpenADR 2.0 demand-response signals by curtailing non-critical electrical loads (lighting dimming, HVAC setpoint relaxation) within 5 minutes while maintaining crop-safe environmental boundaries. | stakeholder-requirements | Stakeholder Requirements |  | Test | 100 |  | Energy Utility/Grid Operator, Daily Growing Cycle: 500kW-2MW facility load incurs significant demand charges. Demand response participation requires automated load shedding within utility-specified response windows while protecting crop viability. | stakeholder, stk-utility, session-462, idempotency:stk-utility-dr-462
STK-REQ-012 | The Vertical Farm Environment Controller SHALL provide the energy utility with 15-minute-interval load forecasts at least 1 hour ahead and confirm curtailment actions within 60 seconds of demand-response event acknowledgement. | stakeholder-requirements | Stakeholder Requirements |  | Test | 100 |  | Energy Utility/Grid Operator: Utility requires load predictability for grid balancing. 15-minute intervals match smart meter granularity. 1-hour forecast horizon enables utility dispatch planning. 60-second curtailment confirmation meets OpenADR fast-DR requirements. | stakeholder, stk-utility, session-462, idempotency:stk-utility-forecast-462
STK-REQ-013 | The Vertical Farm Environment Controller SHALL provide the controls system integrator with documented configuration interfaces for PID tuning parameters, alarm thresholds, network topology, and zone-to-controller mapping, with all configuration changes version-controlled and auditable. | stakeholder-requirements | Stakeholder Requirements |  | Inspection | 100 |  | Controls System Integrator: Commissioning and lifecycle maintenance requires structured access to control parameters. Version-controlled configuration prevents undocumented changes that could cause environmental excursions after maintenance visits. | stakeholder, stk-integrator, session-462, idempotency:stk-integrator-config-462
STK-REQ-014 | The Vertical Farm Environment Controller SHALL support remote firmware updates for zone controllers with rollback capability, executing updates only during scheduled maintenance windows and requiring operator authorisation. | stakeholder-requirements | Stakeholder Requirements |  | Test | 100 |  | Controls System Integrator: Firmware updates are necessary for bug fixes and feature additions over 15-20 year system life. Rollback prevents bricking zone controllers. Maintenance window restriction prevents updates during active crop cycles. Operator authorisation prevents unauthorised changes per IEC 62443. | stakeholder, stk-integrator, session-462, idempotency:stk-integrator-firmware-462
STK-REQ-015 | The Vertical Farm Environment Controller SHALL operate within electromagnetic emission limits per EN 61326-1 and maintain control accuracy within specified tolerances when exposed to ESD, EFT, and surge transients per IEC 61000-4 series in the presence of LED drivers and variable-speed drives. | stakeholder-requirements | Stakeholder Requirements |  | Test | 86 |  | Environment as stakeholder, Electromagnetic constraint: LED drivers (50-200kHz switching) and VSD-equipped HVAC fans generate significant EMI. Controller sensors and communication buses must maintain signal integrity in this electrically noisy environment to prevent false readings or control errors. | stakeholder, stk-environment, session-462, idempotency:stk-env-emc-462
STK-REQ-016 | The Vertical Farm Environment Controller SHALL maintain safe environmental conditions in all zones during and after loss of external network connectivity for a minimum of 72 hours using locally stored crop recipes and control parameters. | stakeholder-requirements | Stakeholder Requirements |  | Test | 100 |  | Environment as stakeholder, Network constraint: Cloud connectivity supports monitoring and analytics but crop safety cannot depend on internet availability. 72-hour autonomy covers typical ISP outage resolution time and ensures crop cycles are not interrupted by IT infrastructure failures. | stakeholder, stk-environment, session-462, idempotency:stk-env-network-resilience-462
SUB-REQ-001 | The CO2 Safety Sensor Array SHALL provide an independent CO2 measurement for each zone, achieving accuracy of ±50 ppm across the 0–10,000 ppm range at a sample rate of 1 Hz, using electrochemical or NDIR sensor technology rated to IEC 61508 SIL 3. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | SYS-REQ-004 mandates an independent safety-rated CO2 sensor separate from the process dosing sensor. Independence prevents common-cause failure: if the process sensor drifts and causes CO2 overdose, the safety sensor provides the credible measurement to trigger the interlock. ±50 ppm accuracy is the specification minimum to discriminate the 5000 ppm trip threshold from normal 1000–2000 ppm operating range. | subsystem, safety-interlock, sil-3, session-463, idempotency:sub-co2-sensor-accuracy-463
SUB-REQ-002 | The CO2 Safety Sensor Array SHALL implement 2-out-of-3 (2oo3) voting across three independently powered sensor channels per zone, such that a single sensor failure does not suppress the CO2 interlock nor generate a spurious trip. | subsystem-requirements | Subsystem Requirements |  | Test | 100 |  | IEC 61511 SIL 3 requires voted redundancy to achieve the required probability of failure on demand (PFD < 10^-3). 2oo3 provides both high availability (tolerates one sensor fail-safe) and high reliability (requires two sensors to agree before triggering, preventing spurious shutdown). This balances crop protection against nuisance trips. | subsystem, safety-interlock, sil-3, session-463, idempotency:sub-co2-sensor-voting-463
SUB-REQ-003 | The Safety PLC SHALL be certified to IEC 61508 SIL 3 using a 2oo2 dual-core architecture with cross-checking, achieving a hardware fault tolerance HFT=1 and diagnostic coverage DC > 99%, with a safe failure fraction SFF > 99%. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | IEC 61508 SIL-3 certification requires physical demonstration of the hardware fault tolerance (HFT=1) and diagnostic coverage (DC>99%) claims, not architectural analysis alone. Verification method changed from Analysis to Inspection: confirm the third-party IEC 61508 SIL-3 certification certificate issued by a Notified Body (TÜV, Bureau Veritas, or equivalent) is present in the project safety case dossier. The certificate must explicitly state SIL-3 capability, the 2oo2 dual-core architecture, HFT=1, DC>99%, and SFF>99%. Certificate inspection satisfies IEC 61511 Clause 11.6.3 which accepts SIL-certified equipment via documented prior use or third-party certification. | subsystem, safety-interlock, sil-3, session-463, idempotency:sub-safety-plc-sil3-463
SUB-REQ-004 | The Safety PLC SHALL complete each execution scan within 50 ms, with a hardware watchdog that forces a safe-state transition if scan completion is not confirmed within 100 ms. | subsystem-requirements | Subsystem Requirements |  | Test | 100 |  | SYS-REQ-004 requires CO2 interlock action within 30 seconds. The 50ms scan cycle provides 600 evaluation cycles within the 30s window, ensuring the interlock logic responds promptly to sensor threshold crossings. The 100ms watchdog ensures software freeze cannot prevent actuator de-energisation, meeting IEC 61511 requirements for safe-state enforcement. | subsystem, safety-interlock, sil-3, session-463, idempotency:sub-safety-plc-scan-463
SUB-REQ-005 | The Voted Logic Engine SHALL evaluate the following trip conditions on every scan and assert the corresponding interlock within the specified response time: CO2 > 5000 ppm (30s), LED surface temperature > 85°C (10s), zone temperature > 38°C (10s), pH dosing excess injection > 5% tank volume in 10 min (5s), emergency stop button pressed (1s). | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | These thresholds and response times are derived directly from SYS-REQ-004, SYS-REQ-007, SYS-REQ-009, and SYS-REQ-013. Grouping all interlock conditions in a single voted logic engine ensures prioritisation conflicts are resolved deterministically. Response times are set to prevent physiological CO2 harm (>30s exposure at >5000 ppm), thermal fixture damage, and crop contamination from excess pH dosing. | subsystem, safety-interlock, sil-3, session-463, idempotency:sub-voted-logic-trips-463
SUB-REQ-006 | When any interlock trip condition is asserted, the Safety Interlock Subsystem SHALL transition all affected zone outputs to the safe state within the condition-specific response time: CO2 isolation valve CLOSED, emergency ventilation OPEN, LED array circuit breakers OPEN, irrigation isolation valves CLOSED. The safe state SHALL be maintained until an authorised operator manually resets the interlock at the Safety PLC HMI. | subsystem-requirements | Subsystem Requirements |  | Demonstration | 86 |  | IEC 61511 requires each SIF to have a defined safe state and a means of demanding that state. De-energised final elements (NC valves closed, NO contactors open) implement fail-safe design: loss of power, wiring break, or PLC failure automatically demands the safe state without active intervention. Manual reset prevents automatic restart into a hazardous condition before root cause is identified. | subsystem, safety-interlock, sil-3, session-463, idempotency:sub-safe-state-def-463
SUB-REQ-007 | The Hardwired Trip Bus SHALL operate entirely via discrete 24VDC relay circuits independent of any fieldbus (MODBUS, Ethernet, CAN), such that failure, disconnection, or compromise of any digital communication network cannot inhibit or delay interlock actuation. | subsystem-requirements | Subsystem Requirements |  | Inspection | 71 |  | SYS-REQ-015 mandates that safety-critical control functions operate independently of the process control network. A cyber event, network flood, or switch failure that disables MODBUS must not prevent CO2 interlock actuation. Hardwired relay independence is the fundamental SIL 3 isolation mechanism required by IEC 61511 clause 11.6 (independence of safety-critical systems). | subsystem, safety-interlock, sil-3, session-463, idempotency:sub-trip-bus-isolation-463
SUB-REQ-008 | The Lockout Tagout Controller SHALL prevent energisation of any zone equipment when a LOTO key for that zone is checked out, and SHALL generate an audible and visual alarm (amber beacon and buzzer) if re-energisation is attempted while a key remains outstanding. | subsystem-requirements | Subsystem Requirements |  | Demonstration | 86 |  | STK-REQ-006 requires lockout/tagout capability for maintenance. OSHA 29 CFR 1910.147 mandates that LOTO devices prevent equipment re-energisation. Hardware enforcement (key-switch interlocked with Safety PLC) is required because software-only LOTO cannot achieve the required reliability — a software bug or reboot could re-enable outputs, endangering maintenance personnel working inside the zone. | subsystem, safety-interlock, sil-1, session-463, idempotency:sub-loto-enforcement-463
SUB-REQ-009 | The Safety PLC SHALL be connected to the process control network via a unidirectional data diode or certified firewall only, such that no inbound network command can modify interlock logic, trip thresholds, or safe-state outputs at runtime. | subsystem-requirements | Subsystem Requirements |  | Inspection | 71 |  | SYS-REQ-015 requires safety functions to operate independently from the process network. A bidirectionally connected Safety PLC is vulnerable to command injection via MODBUS write coils — an attacker or software bug could disable the CO2 interlock remotely. The data diode or certified gateway enforces one-way diagnostic export while preventing any inbound control path, as required by IEC 62443 for safety-instrumented systems. | subsystem, safety-interlock, sil-3, session-463, idempotency:sub-plc-network-isolation-463
SUB-REQ-010 | The Voted Logic Engine SHALL log every interlock state transition — including timestamp (UTC, ±1s accuracy), trigger condition, sensor readings at time of trip, and operator reset identity — to non-volatile memory with capacity for a minimum of 10,000 events, retained through power loss. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | STK-REQ-009 requires tamper-evident environmental records and SYS-REQ-011 requires event logging. Interlock event logs are primary evidence for regulatory investigations (OSHA incident reports, HACCP deviations, insurance claims). Non-volatile storage ensures logs survive a power trip caused by the interlock itself. 10,000 events covers >27 years at one event per day, or >2 years at 15 events per day. | subsystem, safety-interlock, sil-3, session-463, idempotency:sub-voted-logic-audit-463
SUB-REQ-011 | The Safety Interlock Subsystem SHALL support a periodic proof test sequence at intervals not exceeding 12 months, exercising all CO2 sensor channels, voted logic trip conditions, relay outputs, and final element positions, with test results automatically logged and accessible for regulatory review. | subsystem-requirements | Subsystem Requirements |  | Demonstration | 86 |  | IEC 61511 clause 16 requires a proof test interval to detect dangerous undetected failures and maintain the SIL 3 PFD target. Cross-domain analog with nuclear SIL-3 safety logic processors (hex D1B77858) confirms proof test scheduling as a mandatory lifecycle requirement. Without periodic proof testing, latent failures in the hardwired trip bus or sensor channels will accumulate until the SIL 3 PFD target is exceeded. 12-month interval is the maximum permitted under the PFD calculation for this SIL 3 SIF with the selected architecture. | subsystem, safety-interlock, sil-3, session-463, idempotency:sub-proof-test-463
SUB-REQ-012 | The CO2 Injection Controller SHALL execute a per-zone PID control loop with update period ≤100 ms, adjusting Zone Solenoid Valve duty cycle to maintain CO2 concentration within ±50 ppm of the zone setpoint during steady-state enrichment. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | SYS-REQ-003 requires ±50 ppm regulation. The 100ms scan rate is derived from the CO2 injection dynamics: at maximum flow rate the concentration in a 40m³ zone can rise at ~150 ppm/min, so a 100ms control cycle provides >100 samples per ppm rise, giving the PID loop adequate resolution to prevent overshoot. | rt-implausible-value, red-team-session-480
SUB-REQ-013 | The CO2 Injection Controller SHALL accept zone CO2 concentration setpoints in the range 400–2000 ppm at ±1 ppm resolution via Modbus TCP/IP from the Supervisory Control Subsystem, with any setpoint command rejected and alarmed if it falls outside the crop-safe range defined in the active zone recipe. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | SYS-REQ-003 bounds software-controlled CO2 to ≤3000 ppm. Clamping setpoint acceptance at 2000 ppm provides a 1000 ppm margin below the software limit, preventing operator or recipe error from approaching the safety threshold. 400 ppm floor represents atmospheric baseline. | subsystem, co2-enrichment-subsystem, session-465, sil-0, idempotency:sub-co2-ctrl-setpoint-465
SUB-REQ-014 | The CO2 Injection Controller SHALL command all Zone Solenoid Valves to close when any zone CO2 concentration measurement from the Zone NDIR CO2 Sensor Array exceeds 2800 ppm, and SHALL NOT reopen valves until concentration falls below 2500 ppm, implementing an independent software-level concentration ceiling. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | SYS-REQ-003 prohibits software-controlled CO2 exceeding 3000 ppm. The 2800 ppm trip and 2500 ppm reset provide 200 ppm and 500 ppm margins respectively, with hysteresis to prevent valve chatter. This software ceiling is complementary to — and does not replace — the SIL-3 hardware trip at 5000 ppm. | subsystem, co2-enrichment-subsystem, session-465, sil-0, idempotency:sub-co2-ctrl-ceiling-465
SUB-REQ-015 | The Zone NDIR CO2 Sensor Array SHALL provide CO2 concentration measurements in the range 300–3000 ppm with accuracy ±100 ppm (or ±3% of reading, whichever is greater) at 1 Hz sample rate per zone, maintaining accuracy within the specified limits across the temperature range 18–35°C and 40–90% relative humidity. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | ±100 ppm accuracy aligns with the PID controller's ±50 ppm regulation target (2× margin), accounting for sensor drift between calibrations. Temperature and humidity ranges reflect vertical farm grow-room conditions. NDIR technology is preferred over electrochemical for process sensing due to superior stability and lower maintenance than the safety sensors. | rt-implausible-value, red-team-session-480
SUB-REQ-016 | The Zone NDIR CO2 Sensor Array SHALL perform automatic single-point calibration against atmospheric CO2 (nominally 420 ppm) when the grow zone has been unoccupied and ventilated to ambient for ≥30 minutes, with calibration logged including timestamp and pre/post calibration readings. | subsystem-requirements | Subsystem Requirements |  | Demonstration | 86 |  | NDIR sensors drift over time due to LED aging; automatic recalibration during scheduled zone transitions (harvest, replanting) maintains measurement accuracy without manual intervention. Logging enables drift trend analysis and maintenance scheduling. | subsystem, co2-enrichment-subsystem, session-465, sil-0, idempotency:sub-co2-ndir-cal-465
SUB-REQ-017 | The Zone Solenoid Valve Array SHALL achieve a de-energised (closed) state within 500 ms of removal of 24VDC supply, with a spring-return mechanism that maintains the closed position against manifold pressure up to 3 bar without energisation. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | 500 ms valve closure time is driven by the SIL-3 safety loop response budget: SYS-REQ-004 requires full system response (sense + trip + valve close) within 2 seconds; the safety PLC scan budget is ≤50 ms (SUB-REQ-004), leaving 1450 ms for hardwired relay actuation plus valve stroke. Fail-closed on de-energisation is mandatory for CO2 systems to prevent uncontrolled enrichment on power loss. | subsystem, co2-enrichment-subsystem, session-465, sil-3, idempotency:sub-co2-valve-closure-465
SUB-REQ-018 | While de-energised, the Zone Solenoid Valve Array SHALL exhibit a seat leakage rate of ≤0.001 cm³/min at 1.5 bar differential pressure, tested per ISO 15848 Class AH, to prevent CO2 seepage into occupied zones during valve-closed conditions. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | CO2 leakage through closed valves can cause slow concentration creep; at 0.001 cm³/min per valve across 12 zones the total leakage is negligible relative to zone volume (40m³), preventing any measureable rise over an 8-hour unoccupied period. Class AH per ISO 15848 provides an industry-standard leakage acceptance criterion for gas service. | subsystem, co2-enrichment-subsystem, session-465, sil-0, idempotency:sub-co2-valve-leak-465
SUB-REQ-019 | The CO2 Distribution Manifold SHALL maintain zone injection pressure at 1.5 bar ±0.1 bar via a pressure-reducing valve, with a relief valve set to open at 2.5 bar, for all CO2 flow conditions between zero and maximum simultaneous injection to all zones. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | 1.5 bar injection pressure is the design operating point for the solenoid valves' Cv 0.5 rating; ±0.1 bar variance limits flow variation across zones to <7%. Relief valve at 2.5 bar protects valve seals and fittings rated to 3 bar, providing 0.5 bar margin. These values are derived from the valve manufacturers' pressure ratings. | subsystem, co2-enrichment-subsystem, session-465, sil-0, idempotency:sub-co2-manifold-pressure-465
SUB-REQ-020 | The CO2 Distribution Manifold wetted surfaces SHALL be constructed from SS316 stainless steel or PTFE, with all joints using face-seal fittings (Swagelok or equivalent), and SHALL be pressure-tested to 1.5× maximum operating pressure (2.25 bar) before first use. | subsystem-requirements | Subsystem Requirements |  | Inspection | 86 |  | SS316 and PTFE are compatible with high-purity CO2 gas and resist moisture condensation in humid grow-room environments. Face-seal fittings eliminate threaded connections that can work loose from vibration. Pressure test at 1.5× is the standard hydrostatic test factor for piping systems per EN 13480. | subsystem, co2-enrichment-subsystem, session-465, sil-0, idempotency:sub-co2-manifold-material-465
SUB-REQ-021 | When a Zone NDIR CO2 Sensor Array fault is detected for a specific zone (output out of range, diagnostic alarm, or communication failure), the CO2 Injection Controller SHALL close that zone's solenoid valve and raise an alarm within 5 seconds, maintaining CO2 injection to all other zones at their setpoints unaffected. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Sensor fault must trigger valve closure for the affected zone to prevent uncontrolled CO2 accumulation — without a process measurement the PID loop cannot maintain safe bounds. Isolation to one zone preserves production in other zones; 5-second alarm response is derived from the 1Hz sensor scan rate plus two missed scans as a dead-band. | subsystem, co2-enrichment-subsystem, session-465, sil-0, idempotency:sub-co2-ctrl-degraded-sensor-465
SUB-REQ-022 | When the CO2 Enrichment Subsystem receives a safety interlock trip signal via the hardwired de-energise-to-trip relay, all Zone Solenoid Valves SHALL be driven to the closed state within 500 ms regardless of CO2 Injection Controller command state, and the CO2 Injection Controller SHALL lock out all valve open commands until an operator-authorised reset is performed. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | SYS-REQ-004 and SIL-3 allocation require that the safety function (CO2 valve closure on over-concentration) is not defeatable by the process controller. Hardwired override ensures the safety trip action is independent of software state. Operator-authorised reset prevents automatic restart after a SIL-3 trip event, which could re-introduce the hazard before the cause is investigated. This is the safe state for IEC 61508 SIL 3 CO2 injection hazard. | subsystem, co2-enrichment-subsystem, session-465, sil-3, idempotency:sub-co2-safe-state-465
SUB-REQ-023 | The CO2 Injection Controller SHALL operate from a 24VDC ±10% supply at maximum 15W continuous draw, with the supply provided via an uninterruptable power supply (UPS) rated for ≥30 minutes runtime at full load, ensuring CO2 injection control is maintained during mains power interruptions. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Power supply budget is required to size the UPS and cable/fuse ratings. 15W is the maximum for a typical mid-range PLC with full I/O populated. 30 minutes UPS runtime allows for orderly shutdown of grow zones without crop damage from uncontrolled CO2 enrichment during power events. | subsystem, co2-enrichment-subsystem, session-465, sil-0, idempotency:sub-co2-ctrl-power-465
SUB-REQ-024 | The EC/pH Sensor Array SHALL measure electrical conductivity in the range 0.1–10.0 mS/cm with accuracy ±0.1 mS/cm and pH in the range 3.0–9.0 with accuracy ±0.05 pH units, both temperature-compensated to 20°C reference via PT1000 probe, at a measurement rate of 0.1 Hz per zone. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | SYS-REQ-006 mandates EC control within ±0.1 mS/cm of setpoint. A sensor accuracy of ±0.1 mS/cm consumes the full allowable error budget, leaving zero margin for dosing lag and system drift. This accuracy therefore sets the tightest single-sensor limit achievable without disproportionate cost; any looser sensor spec would make the ±0.1 mS/cm system requirement unachievable. The pH ±0.05 accuracy similarly supports the ±0.2 pH system requirement (SYS-REQ-006) with margin. | subsystem, nutrient-management-subsystem, sil-2, session-466, idempotency:sub-ecph-accuracy-466
SUB-REQ-025 | The EC/pH Sensor Array SHALL detect sensor drift or fault conditions — including open-circuit, short-circuit, and out-of-range output — and transmit a fault flag to the Irrigation Controller within 5 seconds of fault onset. | subsystem-requirements | Subsystem Requirements |  | Test | 100 |  | SYS-REQ-007 specifies that repeated dosing without pH equilibration must be treated as potential sensor drift. If the EC/pH Sensor Array cannot self-report a fault, the Irrigation Controller will continue commanding the Dosing Pump Array based on a stale or stuck reading, leading to cumulative overdosing and safety interlock activation. The 5-second detection window allows at most one additional 0.1Hz measurement before the fault is visible to the controller. | subsystem, nutrient-management-subsystem, sil-2, session-466, idempotency:sub-ecph-fault-466
SUB-REQ-026 | The Dosing Pump Array SHALL deliver each individual pump injection with a stroke volume accuracy of ±1% of commanded volume, with maximum single-stroke volume not exceeding 2% of working solution tank volume, verified by encoder-counted revolutions. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | SYS-REQ-006 explicitly limits dosing pump stroke volume to 2% of tank volume per injection to prevent overshoot. A ±1% stroke accuracy ensures the commanded 2% limit is not inadvertently exceeded by pump calibration error alone. Without this accuracy requirement, a pump running 10% high on stroke volume could exceed the watchdog threshold (5% cumulative over 10 minutes) within 3 injections at nominal setpoints. | subsystem, nutrient-management-subsystem, sil-2, session-466, idempotency:sub-dpa-stroke-accuracy-466
SUB-REQ-027 | The Dosing Pump Array SHALL implement a hardwired cumulative injection counter that monitors total acid and base pump volume delivered within any rolling 10-minute window, and SHALL assert a 24VDC normally-open fault contact to the Safety PLC within 200 ms when cumulative injection exceeds 5% of the working solution tank volume within that window. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | SYS-REQ-007 and SYS-REQ-015 require the dosing-excess protection function to meet SIL-2. Implementing this watchdog as a hardwired counter in the pump drive firmware rather than as a software function in the Irrigation Controller is consistent with ARC-REQ-001 and ARC-REQ-006 — safety-critical shutdown functions must not rely on general-purpose software. The 200ms propagation time matches IFC-REQ-019 and ensures the Safety PLC trip logic executes before a second injection cycle can begin (minimum pump cycle time is >500ms). | subsystem, nutrient-management-subsystem, sil-2, safety, session-466, idempotency:sub-dpa-watchdog-466
SUB-REQ-028 | When the Dosing Pump Array receives a hardwired interlock trip signal from the Safety PLC (IFC-REQ-019 signal path), the Dosing Pump Array SHALL inhibit all pump outputs and de-energise all pump drive signals within 500 ms, and SHALL not resume dosing until the interlock is manually reset. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | IEC 61508 SIL-2 requires a safe state for every safety-critical function. The safe state for overdosing hazard (SYS-REQ-007) is cessation of all dosing. The 500ms response time allows for one PLC scan cycle (50ms) plus drive inhibit propagation. Manual reset prevents autonomous restart after a dosing-excess event, which must be investigated before resuming operation. | subsystem, nutrient-management-subsystem, sil-2, safety, session-466, idempotency:sub-dpa-safe-state-466
SUB-REQ-029 | The Irrigation Controller SHALL execute configurable zone irrigation schedules with on-time resolution of ±1 minute over a 24-hour period, supporting drip and flood-drain (NFT) modes, and SHALL enforce a minimum 5-minute inter-zone delay to prevent simultaneous multi-zone demand exceeding recirculation pump rated flow. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Simultaneous activation of more than approximately 60% of zone valves at peak flow exceeds the recirculation pump rated capacity (300 L/min), causing pressure drop across the furthest zones and uneven nutrient distribution. The 5-minute inter-zone delay ensures sequential activation scheduling that keeps total demand within pump capacity. | subsystem, nutrient-management-subsystem, session-466, idempotency:sub-ic-scheduling-466
SUB-REQ-030 | The Irrigation Controller SHALL detect a stuck-open zone irrigation valve condition within 30 seconds by comparing commanded valve state (closed) against flow meter measurement exceeding 2 L/min on the corresponding zone header, and SHALL command the zone isolation valve closed and activate floor drain pumps within 60 seconds of detection. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | SYS-REQ-010 mandates 30-second stuck-valve detection and 60-second drain pump activation. The 2 L/min threshold is set above instrument noise (flow meter accuracy ±2% at 100 L/min full scale = ±2 L/min) while remaining sensitive enough to detect a single failed-open 15mm solenoid valve (minimum flow ~8 L/min at 1.2 bar). Without this requirement cascaded to the Irrigation Controller, SYS-REQ-010 lacks a component responsible for the detection logic. | subsystem, nutrient-management-subsystem, sil-2, safety, session-466, idempotency:sub-ic-stuck-valve-466
SUB-REQ-031 | The Irrigation Controller SHALL execute zone sanitisation sequences on command, including: circulating peracetic acid solution at ≥80 ppm concentration for ≥20 minutes contact time, flushing until EC/pH Sensor Array confirms rinse water EC <0.3 mS/cm and pH 6.5–7.0, and confirming drain completion via sump level sensor, before setting the zone-ready flag that permits new crop recipe activation. | subsystem-requirements | Subsystem Requirements |  | Demonstration | 86 |  | SYS-REQ-016 blocks crop recipe activation until sanitisation criteria pass. The specific parameters (≥80 ppm peracetic acid, ≥20 minutes contact time) are derived from food-safety CIP (clean-in-place) protocols for hydroponic systems per GLOBALG.A.P. and UK food safety guidance — lower concentrations or shorter contact times do not reliably achieve the 5-log pathogen reduction required for fresh produce food safety. | subsystem, nutrient-management-subsystem, compliance, session-466, idempotency:sub-ic-sanitisation-466
SUB-REQ-032 | The Zone Irrigation Valve Array SHALL use normally-closed solenoid valves that achieve full seat closure within 2 seconds of de-energisation, with EPDM seat leakage not exceeding 0.5 mL/min at 2.5 bar differential, maintaining fail-safe closed state on loss of 24VAC supply. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Fail-safe closure on power loss prevents irrigation from continuing during an electrical fault or emergency shutdown. The 2-second closure time ensures that stuck-valve detection response (SYS-REQ-010, 30s) has no ambiguity about valve state. Seat leakage ≤0.5 mL/min is necessary to prevent slow flooding accumulation in the grow bed during extended power-off periods; a failed valve leaking at higher rates would accumulate water over hours even in shutdown state. | subsystem, nutrient-management-subsystem, sil-2, safety, session-466, idempotency:sub-ziva-failsafe-466
SUB-REQ-033 | Each solenoid valve in the Zone Irrigation Valve Array SHALL provide a reed-switch position feedback signal (24VDC open-collector) confirming open or closed state within 2 seconds of the commanded transition, detectable by the Irrigation Controller as a discrete digital input. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Position feedback is required by the stuck-valve detection logic (SUB-REQ-030) to distinguish between a genuinely stuck valve and a valve that has been commanded closed but not yet physically settled. Without confirmed position feedback, the Irrigation Controller cannot determine whether continued flow is caused by valve failure or normal settling delay, leading to premature false alarms or missed detections. | subsystem, nutrient-management-subsystem, session-466, idempotency:sub-ziva-feedback-466
SUB-REQ-034 | The Recirculation Pump System SHALL operate in duty/standby configuration with automatic changeover to the standby pump within 30 seconds of detecting duty pump failure (loss of flow confirmation >10 L/min below setpoint for 15 seconds), maintaining nutrient solution circulation without operator intervention. | subsystem-requirements | Subsystem Requirements |  | Demonstration | 86 |  | A single recirculation pump failure interrupting nutrient flow for more than approximately 15 minutes causes crop stress in nutrient-film technique (NFT) channels where root zone drying begins rapidly. Duty/standby with 30-second changeover limits maximum interruption to under 1 minute, well within the 15-minute crop stress threshold. This justification also underpins the ARC-REQ-006 decision to use dual pumps rather than a single high-reliability unit. | subsystem, nutrient-management-subsystem, session-466, idempotency:sub-rps-standby-466
SUB-REQ-035 | The Recirculation Pump System SHALL detect dry-run conditions within 10 seconds using a flow switch confirming <5 L/min on the pump outlet with the pump energised, and SHALL de-energise the pump motor and inhibit restart for a minimum 60-second cool-down period to prevent seal and impeller damage. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Peristaltic seal failure due to dry running can release pump materials into the nutrient solution, contaminating the food crop. The 10-second detection window (100 pump revolutions at minimum speed) is fast enough to stop seal damage before contamination risk. The 60-second inhibit prevents repeated auto-restart cycling that accelerates bearing wear and could mask an empty reservoir alarm. | rt-implausible-value, red-team-session-480
SUB-REQ-036 | The Nutrient Reservoir and Mixing System SHALL trigger a low-level alarm on the Supervisory Control Subsystem when the working solution reservoir volume falls below 20% of rated capacity, and SHALL trigger an emergency shutdown request to the Irrigation Controller when volume falls below 5% of rated capacity to prevent pump dry-run. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | A 20% low-level alarm gives operators approximately 30 minutes at maximum flow (300 L/min pump rate) to respond before the 5% emergency threshold is reached, providing adequate warning without frequent nuisance alarming. The 5% emergency level is set above the physical minimum needed to keep pump inlet submerged under all orientation conditions, preventing dry-run before the level sensor detects the state. | subsystem, nutrient-management-subsystem, session-466, idempotency:sub-nrm-low-level-466
SUB-REQ-037 | When one EC/pH Sensor Array probe reports a fault in a zone, the Nutrient Management Subsystem SHALL continue closed-loop control of the unaffected measurement parameter (EC or pH) and SHALL operate the affected parameter in open-loop time-based dosing at the last valid recipe setpoint, maintaining dosing frequency not exceeding 50% of the nominal closed-loop rate, until the probe fault is cleared or manually acknowledged. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | A complete suspension of dosing on any sensor fault would halt crop nutrition for the entire zone, causing crop loss disproportionate to the fault severity. Continued unaffected-parameter control and reduced-rate open-loop dosing on the faulted parameter limits crop risk while preventing the unconstrained dosing that a full open-loop mode without rate reduction would allow. The 50% rate reduction provides sufficient safety margin against overdosing while maintaining minimum nutrient delivery. | subsystem, nutrient-management-subsystem, sil-2, session-466, idempotency:sub-nm-degraded-mode-466
SUB-REQ-039 | The Horticultural Lighting Subsystem SHALL maintain zone PPFD within ±5% of the crop recipe PAR setpoint across the 100-600 µmol/m²/s operating range under steady-state conditions. | subsystem-requirements | Subsystem Requirements |  | Test | 100 |  | SYS-REQ-005 allocates ±5% PAR accuracy to this subsystem. ±5% is the agronomic boundary within which the LCU's PAR PID loop can hold steady state; exceeding this boundary causes measurable yield loss and recipe non-compliance. Derived from crop science DLI (Daily Light Integral) tolerance data. | subsystem, horticultural-lighting, sil-2, session-467, idempotency:sub-hls-par-accuracy-467
SUB-REQ-040 | The Lighting Control Unit SHALL control each of the four spectrum channels (red 660nm, blue 450nm, white 4000K, far-red 730nm) independently with 12-bit or greater PWM dimming resolution over a 0-100% intensity range. | subsystem-requirements | Subsystem Requirements |  | Test | 100 |  | Twelve-bit resolution (4096 steps) provides 0.024% per step, which keeps spectral accuracy within the 0.5% per-step ramp requirement of SUB-HVAC-004 and supports the recipe spectrum ratio requirements of the crop science protocol. Lower resolution (10-bit) causes visible stepping artefacts on long ramps. | subsystem, horticultural-lighting, session-467, idempotency:sub-hls-spectral-resolution-467
SUB-REQ-041 | The Lighting Control Unit SHALL execute linear intensity ramp transitions between setpoints over operator-configurable periods of 5, 10, 15, 20, or 30 minutes with ramp step size not exceeding 0.5% of full scale per step. | subsystem-requirements | Subsystem Requirements |  | Test | 100 |  | Abrupt light transitions cause photoinhibition stress in leafy crops by overwhelming the photosystems before protective down-regulation activates. Stepwise ramps over 5-30 minutes are the agronomically recommended range for vertical farms with sensitive leafy crops. | subsystem, horticultural-lighting, session-467, idempotency:sub-hls-intensity-ramp-467
SUB-REQ-042 | When any LED fixture heatsink temperature exceeds 85 degrees C as detected by the Fixture Thermal Monitoring Array hardwired comparator circuit, the Horticultural Lighting Subsystem SHALL de-energise all LED Driver Modules in the affected zone within 2 seconds, independently of the Lighting Control Unit software. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | SYS-REQ-009 allocates the 85 degree C thermal shutdown to this subsystem at SIL 2 (H-002: LED fixture fire hazard). The 2-second maximum is derived from thermal runaway propagation modelling — heat sink temperatures above 85 degree C indicate junction temperatures approaching LED derating limits. The software-independent path is required because SIL 2 prohibits the safety function from relying on general-purpose software per IEC 61508 clause 7.4.2.3. | subsystem, horticultural-lighting, sil-2, session-467, idempotency:sub-hls-thermal-trip-467
SUB-REQ-043 | When any LED fixture heatsink temperature exceeds 75 degrees C, the Lighting Control Unit SHALL reduce LED power in the affected zone by 5% of current output per minute until heatsink temperature falls below 70 degrees C or all driver outputs reach zero. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | A 75 degree C software derating threshold (below the 85 degree C hardware trip) provides a 10-degree C guard band for graceful power reduction before the SIL-2 trip activates, avoiding unnecessary safety shutdowns during moderate load events while still protecting fixtures from thermal damage. | subsystem, horticultural-lighting, sil-2, session-467, idempotency:sub-hls-thermal-derating-467
SUB-REQ-044 | When the zone HVAC compressor trip signal is received from the Zone Controller Network, the Lighting Control Unit SHALL reduce LED power in the affected zone to 50% of the current recipe setpoint within 30 seconds. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | SYS-REQ-008 allocates the 50% LED power reduction upon HVAC trip to this subsystem. LED fixtures contribute 30-40% of zone heat load; reducing output by 50% lowers zone air temperature rise rate by 15-20 degrees C/hour, buying time for the HVAC fault to be resolved before reaching the 38 degree C thermal protection threshold. | subsystem, horticultural-lighting, session-467, idempotency:sub-hls-hvac-loadshed-467
SUB-REQ-045 | When the emergency shutdown signal is asserted on the Safety Interlock hardwired trip bus, the Horticultural Lighting Subsystem SHALL de-energise all LED Driver Modules across all 8 zones within 5 seconds. | subsystem-requirements | Subsystem Requirements |  | Test | 100 |  | SYS-REQ-013 specifies a 10-second emergency shutdown sequence for the full system. LED de-energisation is the first step — removing 400kW+ of electrical load reduces fire risk and allows safe human entry. The 5-second sub-budget allows the remaining 5 seconds for CO2 valve closure and ventilation activation. | subsystem, horticultural-lighting, sil-2, session-467, idempotency:sub-hls-emergency-shutdown-467
SUB-REQ-046 | When a PAR Sensor Array signal is lost or out-of-range in a zone, the Lighting Control Unit SHALL continue closed-loop operation at the last valid setpoint PWM value for up to 4 hours, generate a sensor fault alarm, and transition to full manual override after the 4-hour timeout. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | PAR sensor failure should not immediately force operator intervention in a 24/7 automated facility. A 4-hour hold at last-known PWM is safe because short-term DLI deviation from single-zone sensor loss is within crop tolerance windows. Beyond 4 hours the risk of undetected environmental change justifies requiring operator confirmation. | subsystem, horticultural-lighting, session-467, idempotency:sub-hls-par-degraded-467
SUB-REQ-047 | The PAR Sensor Array SHALL have NIST or PTB-traceable calibration per ASTM E948 with a maximum measurement uncertainty of 3% (k=2) at recalibration intervals not exceeding 12 months. | subsystem-requirements | Subsystem Requirements |  | Inspection | 100 |  | ASTM E948 is the primary standard for PAR sensor calibration in horticultural applications. 3% calibration uncertainty is the maximum consistent with maintaining overall PAR accuracy of ±5% (SYS-REQ-005) when combined with installation and measurement losses. Twelve-month recalibration intervals are standard in controlled horticulture environments per EN ISO 9001 measurement system requirements. | subsystem, horticultural-lighting, session-467, idempotency:sub-hls-par-calibration-467
SUB-REQ-048 | The LED Driver Module Array SHALL achieve a minimum power conversion efficiency of 93% at rated load and maintain output current regulation within 2% of the commanded setpoint under steady-state conditions across all channels. | subsystem-requirements | Subsystem Requirements |  | Test | 100 |  | 93% driver efficiency is the industry minimum for horticultural LED drivers at this power density (>50W per channel). Below 93% the waste heat per zone exceeds the HVAC cooling budget, requiring oversized cooling infrastructure. 2% current regulation translates to 2% PAR variation at constant flux, which must be accounted for in the ±5% overall PAR budget. | subsystem, horticultural-lighting, session-467, idempotency:sub-hls-driver-efficiency-467
SUB-REQ-049 | The Zone Controller Network SHALL provide a supervisory override channel that, when asserted by the Supervisory Control Subsystem within 500 ms, suspends autonomous zone regulation and transfers zone actuator control to the supervisory setpoint within that response window. | subsystem-requirements | Subsystem Requirements | event | Test | 86 |  | UHT classifies zone controller network (51F77808) as Functionally Autonomous (bit 15), requiring an explicit human-in-the-loop override per IEC 62443-3-3 SR 2.12. Without this, the operator cannot regain control during runaway CO2 or thermal excursion scenarios. | idempotency:qc-468-zone-ctrl-net-override
SUB-REQ-050 | The Irrigation Controller SHALL operate from a 24 VDC ±10% supply with a maximum steady-state power consumption of 15 W and a peak inrush current not exceeding 2 A for more than 50 ms at power-on. | subsystem-requirements | Subsystem Requirements | ubiquitous | Test | 86 |  | UHT classifies the irrigation controller (D1F77A08) as Powered (bit 4) and System-Essential (bit 16). Without a defined power envelope, the electrical panel and UPS sizing cannot be verified, and inrush from multiple controllers starting simultaneously could trip circuit protection. | idempotency:qc-468-irrig-ctrl-power
SUB-REQ-051 | The Dosing Pump Array SHALL operate from a 24 VDC ±10% supply with a maximum steady-state power consumption of 30 W per pump and food-contact-compliant wetted materials certified to FDA 21 CFR 177 for nutrient solution compatibility. | subsystem-requirements | Subsystem Requirements | ubiquitous | Test | 86 |  | UHT classifies the dosing pump array (D7F73218) as Powered (bit 4), Physical Medium (bit 7), and Regulated (bit 28). Dosing pumps in a food-production environment require both a defined power budget for UPS autonomy and material certification to prevent nutrient contamination from pump wetted surfaces. | idempotency:qc-468-dosing-pump-power
SUB-REQ-052 | The Supervisory Control Subsystem SHALL authenticate all remote HMI sessions using multi-factor credentials (username/password plus time-based OTP) and SHALL encrypt all management communications using TLS 1.3 or later. | subsystem-requirements | Subsystem Requirements | ubiquitous | Test | 100 |  | UHT classifies the supervisory control subsystem (51BD7908) as Digital/Virtual (bit 24) and Human-Interactive (bit 13). Unauthenticated access to the supervisory HMI would allow an adversary to disable safety interlocks or alter crop recipes; TLS 1.3 prevents credential interception on uncontrolled network segments. | idempotency:qc-468-supervisory-cybersec
SUB-REQ-053 | The Climate Management Subsystem SHALL maintain grow zone air temperature within ±1.0°C of the crop-specific temperature setpoint across the full 18–28°C operating range under steady-state conditions. | subsystem-requirements | Subsystem Requirements |  | Test | 100 |  | Derived from SYS-REQ-001. Temperature deviations beyond ±1.0°C reduce crop growth rate and quality; validated against industry benchmarks for lettuce (20±1°C), strawberry (18±1°C), and basil (22±1°C). The ±1.0°C band is the tightest achievable with DX HVAC at the specified zone volumes. | rt-implausible-value, red-team-session-480
SUB-REQ-054 | The Climate Management Subsystem SHALL maintain grow zone relative humidity within ±5% RH of the crop-specific humidity setpoint across the 60–85% RH operating range under steady-state conditions. | subsystem-requirements | Subsystem Requirements |  | Test | 100 |  | Derived from SYS-REQ-002. RH deviations beyond ±5% promote fungal pathogens (Botrytis cinerea) at high end and cause crop tip-burn through reduced transpiration at low end. The ±5% band is the IEC 61511 functional accuracy class for capacitive RH sensors in the 0–40°C temperature compensation range. | subsystem, climate-management, session-469, idempotency:sub-cms-rh-regulation-469
SUB-REQ-055 | When the HVAC Actuator Interface reports a compressor trip condition, the Zone Climate Controller SHALL send a lighting load-reduction command to the Supervisory Control Subsystem within 500 ms and engage the economiser damper to maintain zone temperature below 30 degC. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Derived from SYS-REQ-008. Compressor trip causes loss of cooling capacity; LED fixtures contribute up to 40 percent of zone heat load, so reducing lighting is the fastest mechanical intervention available. The 500 ms response window was derived from the thermal time constant analysis for a 20 m2 zone under peak summer ambient conditions. | subsystem, climate-management, session-469, idempotency:sub-cms-compressor-trip-469
SUB-REQ-056 | The Temperature Sensor Network SHALL sample all zone temperature sensors at a minimum rate of 1 Hz and deliver readings to the Zone Climate Controller with a maximum end-to-end latency of 2 s from measurement to controller input. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | 1 Hz sampling is the minimum required for PID loop stability given the thermal time constant of the grow zone air volume (estimated 60-90 s). The 2 s maximum latency bound ensures the PID derivative term is not corrupted by stale data during transient events such as door opening. | subsystem, climate-management, session-469, idempotency:sub-cms-temp-sampling-469
SUB-REQ-057 | When the Temperature Sensor Network detects a sensor reading outside the valid range of 0 to 50 degC or reports a wire-break fault, the Zone Climate Controller SHALL switch control inputs to the next available redundant sensor and generate a maintenance alarm within 30 s. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Dual-sensor redundancy per zone (top and bottom canopy positions) ensures continued closed-loop control on single sensor failure. The 30 s alarm latency allows operator awareness before the next crop inspection round while not imposing real-time alarm fatigue. | subsystem, climate-management, session-469, idempotency:sub-cms-sensor-fault-469
SUB-REQ-058 | The Fresh Air Ventilation Controller SHALL coordinate fresh air fraction with the CO2 Enrichment Subsystem via Modbus TCP, maintaining a fresh air fraction between 5 and 30 percent of zone supply volume to balance CO2 setpoint, O2 replenishment, and ethylene dilution requirements. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Derived from the need to manage competing gas concentrations without independent control of each. The 5-30 percent range is the mechanical limit of the HRV unit specified; below 5 percent O2 depletion risk rises; above 30 percent the CO2 enrichment system cannot maintain setpoint economically. Modbus TCP interface selected because CO2 Enrichment Subsystem already uses this bus. | subsystem, climate-management, session-469, idempotency:sub-cms-fresh-air-469
SUB-REQ-059 | The HVAC Actuator Interface SHALL execute Zone Climate Controller setpoint commands within 500 ms of receipt and confirm execution status to the controller within 1 s, for all actuator types (VFD, contactor, modulating valve, damper). | subsystem-requirements | Subsystem Requirements |  | Test | 100 |  | 500 ms command execution latency is the maximum allowed to maintain PID loop stability. Confirmation within 1 s allows the Zone Climate Controller to detect actuator stuck-open/closed conditions and escalate to the Safety Interlock Subsystem if needed. | subsystem, climate-management, session-469, idempotency:sub-cms-actuator-latency-469
SUB-REQ-060 | When a zone isolation command is received from the Safety Interlock Subsystem, the HVAC Actuator Interface SHALL close zone supply and return HVAC dampers within 2 s of command receipt and hold the closed state until an explicit release command is received. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Derived from SYS-REQ-014. Zone airflow isolation prevents spread of pathogens or chemical contamination from an affected zone to adjacent zones via the shared duct network. The 2 s damper closure time is the maximum achievable with the specified 24V spring-return actuators at operating temperature range. | subsystem, climate-management, session-469, idempotency:sub-cms-zone-isolation-469
SUB-REQ-061 | When the Demand Response Handler receives an OpenADR 2.0b demand-response signal from the utility VTN, the Supervisory Control Subsystem SHALL compute and execute a load-reduction plan within 60 s of signal receipt, reducing facility electrical load by the requested amount while maintaining crop-safe minimum environmental parameters. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Derived from SYS-REQ-012. The 60 s execution window is the maximum allowed under OpenADR 2.0b SIMPLE event type baseline specification. Crop-safe minimum parameters (minimum temperature floor, minimum CO2 level) are required to prevent crop loss during DR events that may last up to 4 hours. | subsystem, supervisory-control, session-469, idempotency:sub-scs-dr-response-469
SUB-REQ-062 | When an emergency shutdown trigger is received by the Emergency Shutdown Sequencer (fire alarm relay, manual E-stop, or critical sensor fault), the Supervisory Control Subsystem SHALL complete the full shutdown sequence (CO2 valve closure, nutrient pump off, lighting off, HVAC dampers to purge) within 10 s of trigger receipt. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Derived from SYS-REQ-013. The 10 s total sequence time is driven by the CO2 concentration rise rate in a sealed zone: at maximum CO2 enrichment flow rate, CO2 can rise from 1500 ppm to 5000 ppm (safety limit) in approximately 45 s, giving the sequence a 35 s safety margin. Steps are serialised with the CO2 valve first to maximise margin for that hazard. | subsystem, supervisory-control, session-469, idempotency:sub-scs-emergency-shutdown-469
SUB-REQ-063 | The Supervisory Control Subsystem SHALL execute and verify the zone sanitisation sequence (pH 2.0 flush, UV-C exposure, dry-out dwell) per the registered crop transition protocol before authorising zone reactivation for a new crop cycle, with a verification record written to the compliance audit log. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Derived from SYS-REQ-016. Sanitisation verification is a regulatory and food-safety requirement (GFSI/SQF for leafy greens). Automated verification and audit logging prevents manual bypass and provides the evidence trail required for food safety audits. | subsystem, supervisory-control, session-469, idempotency:sub-scs-sanitisation-469
SUB-REQ-064 | The Crop Recipe Engine SHALL continue executing the active crop recipe and issuing environmental setpoints during Plant Management Server software updates, with setpoint output interruption not exceeding 30 s during the update window. | subsystem-requirements | Subsystem Requirements |  | Test | 100 |  | Crop recipes running 7-120 day cycles cannot tolerate unplanned setpoint loss during routine server maintenance. A 30 s setpoint interruption is within the thermal and CO2 time constants of all grow zones (minimum 60 s), meaning the environment will not deviate beyond crop-safe limits during the gap. | subsystem, supervisory-control, session-469, idempotency:sub-scs-recipe-continuity-469
SUB-REQ-065 | The Zone Controller Unit SHALL maintain closed-loop control of all zone environmental parameters (temperature, humidity, CO2, PAR, pH, EC) within crop recipe setpoints using locally stored setpoint data for a minimum of 30 minutes when the OPC-UA connection to the Zone Edge Gateway is interrupted. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | SYS-REQ-017 requires restoration of zone regulation within 30s of primary node failure. The ZCU must operate autonomously during any switchover period to prevent crop damage, using NOR flash-stored setpoints as the last-valid recipe. 30 minutes exceeds the expected switchover time plus manual response window. | subsystem, zone-controller-network, session-470, idempotency:sub-zcn-zcu-autonomous-470
SUB-REQ-066 | The Zone Controller Unit SHALL execute PID control loop iterations for all regulated environmental parameters at a minimum cycle rate of 10 Hz, with loop execution jitter not exceeding ±5 ms. | subsystem-requirements | Subsystem Requirements |  | Test | 100 |  | SYS-REQ-001 requires ±1.0°C temperature regulation and SYS-REQ-002 requires ±5% RH. Analysis of zone thermal mass and HVAC actuator response times shows that a 10Hz loop rate is the minimum to achieve these tolerances without oscillation. Jitter constraint prevents control loop aliasing against the 10s temperature sensor averaging window. | rt-implausible-value, red-team-session-480
SUB-REQ-067 | The Zone Controller Unit SHALL persist the current active recipe setpoints to non-volatile NOR flash memory within 5 seconds of any setpoint update, and SHALL retrieve stored setpoints within 10 seconds of power restoration. | subsystem-requirements | Subsystem Requirements |  | Test | 100 |  | Required to support the 30-minute autonomous operation window (SUB-REQ-065): setpoints must survive power cycling and network outage. 5s write window is bounded by the PID loop update frequency; 10s retrieval ensures zone control resumes within the SYS-REQ-017 30s failover window. | rt-implausible-value, red-team-session-480
SUB-REQ-068 | The Zone I/O Expansion Module SHALL sample all connected 4-20mA analog inputs at a minimum rate of 1 Hz with ±0.1% full-scale measurement accuracy, and SHALL detect and report open-circuit loop faults on any 4-20mA channel to the Zone Controller Unit within 1 second of fault occurrence. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | SYS-REQ-011 requires 1-second resolution data logging; the I/O Module must sample at least as fast. ±0.1% FSR accuracy corresponds to ±0.16mA on a 20mA span, which resolves to ±0.16°C for a PT100 transmitter — within the sensor measurement error budget. Open-circuit detection within 1s prevents undetected sensor loss from causing uncontrolled dosing. | subsystem, zone-controller-network, session-470, idempotency:sub-zcn-iom-sampling-470
SUB-REQ-069 | The Zone Edge Gateway SHALL aggregate OPC-UA data from all Zone Controller Units and publish an updated node namespace to the Supervisory Control Subsystem at a maximum end-to-end latency of 500 ms from sensor sampling to supervisory data availability. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | SYS-REQ-018 requires real-time zone status display for operator HMI; 500ms end-to-end latency is the human-perceptible update threshold for operational dashboards. This budget is allocated as: 100ms ZCU scan, 100ms RS-485 transfer, 100ms ZCU OPC-UA publish, 100ms network transit, 100ms Gateway aggregation, leaving 100ms margin. | subsystem, zone-controller-network, session-470, idempotency:sub-zcn-gateway-latency-470
SUB-REQ-070 | The Time-Series Database Engine SHALL ingest environmental sensor data at a minimum rate of 1 sample per second per channel across all zones without data loss, and SHALL retain raw 1-second resolution data for a minimum of 90 days and 1-minute resolution aggregates for a minimum of 10 years. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | SYS-REQ-011 requires 1-second resolution logging with 10-year retention. The 90-day raw tier covers the regulatory inspection window for fresh produce (most jurisdictions require 90-day post-harvest environmental records); the 10-year aggregate tier covers long-term trend analysis and facility-level regulatory audits. Loss-free ingestion is required because data gaps invalidate compliance records. | subsystem, data-acquisition, session-470, idempotency:sub-dac-tsdb-ingest-470
SUB-REQ-071 | The Time-Series Database Engine SHALL export any requested date range of environmental data for a specified zone as a CSV file within 30 seconds for queries spanning up to 90 days of 1-second resolution data. | subsystem-requirements | Subsystem Requirements |  | Test | 100 |  | SYS-REQ-011 specifies CSV export within 30 seconds; this requirement constrains the TSDB query engine and storage performance to support that SLA. 90-day scope covers the maximum raw-resolution retention window and defines the worst-case query performance target. | subsystem, data-acquisition, session-470, idempotency:sub-dac-tsdb-export-470
SUB-REQ-072 | The OpenADR Virtual End Node SHALL receive and acknowledge OpenADR 2.0b DR event signals from the utility Virtual Top Node within 30 seconds of event distribution, and SHALL translate the event payload into an energy curtailment command dispatched to the Supervisory Control Subsystem within 5 seconds of acknowledgement. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | SYS-REQ-012 requires response to OpenADR 2.0 demand-response events. Utility OpenADR 2.0b contracts typically specify 30-second acknowledgement SLA; the 5-second internal dispatch ensures the Supervisory has adequate time to pre-condition zones before the event start time. | subsystem, data-acquisition, session-470, idempotency:sub-dac-oadr-dispatch-470
SUB-REQ-073 | The Crop Recipe Database SHALL store a minimum of 200 crop recipes with complete version history, and SHALL maintain an immutable audit trail of all recipe create, update, and supersede operations with timestamp, user identity, and change summary, ensuring no recipe version is ever deleted. | subsystem-requirements | Subsystem Requirements |  | Inspection | 86 |  | SYS-REQ-020 requires 200 crop recipes. Immutable version history with audit trail is required for GMP compliance (21 CFR Part 11 equivalent for food production): regulators require proof that a specific recipe version was active during a specific crop production run, and that recipe changes were authorised. | subsystem, data-acquisition, session-470, idempotency:sub-dac-recipe-db-capacity-470
SUB-REQ-074 | The Compliance Report Generator SHALL produce a zone sanitisation verification report including sensor evidence of peracetic acid contact time, temperature, and concentration, cryptographically signed with a SHA-256 hash of the source TSDB data, within 60 seconds of a sanitisation cycle completion event. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | SYS-REQ-016 requires sanitisation sequence verification including peracetic acid contact time records. The cryptographic hash links the report to immutable TSDB source data, satisfying tamper-evidence requirements for food safety audits (GFSI, SQF). 60-second generation time allows the report to be available before the operator logs off the cleaning shift. | subsystem, data-acquisition, session-470, idempotency:sub-dac-compliance-report-470
SUB-REQ-075 | When the Zone Climate Controller loses communication with the Zone Controller Unit for more than 5 seconds, the Zone Controller Unit SHALL revert to its last valid setpoint cache and maintain that environmental state for at least 15 minutes before declaring a zone fault. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | UHT classifies the Zone Climate Controller (hex D1F77008) as System-Essential (bit 16). Lint finding: zone controller lacks redundancy/failover requirements. The 5-second timeout and 15-minute holdover are derived from the crop thermal time constant — a vertical farm growing zone can tolerate 15 minutes of fixed-setpoint control before temperature drifts outside acceptable bounds, giving maintenance personnel time to respond without triggering a full zone shutdown. | subsystem, zone-controller-network, redundancy, session-471, idempotency:sub-zcn-zcu-holdover-471
SUB-REQ-076 | The CO2 Enrichment Subsystem SHALL incorporate an independent safety-rated CO2 sensor, certified to IEC 61508 SIL-2, operating on a separate power supply and signal path from the process-control CO2 sensors, with a response time not exceeding 30 seconds for a step change from 0 to 5000 ppm. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | SYS-REQ-004 requires the safety interlock to act within 2 seconds on CO2 exceeding 5000 ppm using an independent safety-rated sensor — explicitly separate from the software-controlled process sensor. This SUB requirement derives that sensor's SIL-2 certification, independent power path, and 30-second response time. The 30-second response budget is the 2-second interlock latency padded for sensor settling; IEC 61508 SIL-2 certification is required because CO2 asphyxiation meets the hazard frequency and severity threshold for SIL-2 per the hazard register. | subsystem, co2-enrichment, safety, sil-2, session-471, idempotency:sub-co2-safety-sensor-sil2-471
SUB-REQ-077 | The Zone Controller Network SHALL enforce network segmentation using VLAN isolation between OT zone control traffic and corporate IT networks, with all OPC-UA communications authenticated using X.509 certificates and all Modbus RTU segments accessible only via physically secured electrical enclosures. | subsystem-requirements | Subsystem Requirements |  | Inspection | 86 |  | UHT classifies the zone and associated digital control systems with the Digital/Virtual trait (bit 24), triggering a cybersecurity gap finding in lint. Vertical farm control systems are OT environments with ICS/SCADA attack surfaces: an attacker gaining access to the zone Modbus segments could manipulate CO2 injection solenoids, nutrient dosing pumps, or LED circuits, creating both crop loss and personnel safety risks. VLAN segmentation with X.509 OPC-UA authentication and physical enclosure access control aligns with IEC 62443-3-3 SR 1.1 (identification and authentication) at Security Level 2. | subsystem, zone-controller-network, cybersecurity, session-471, idempotency:sub-zcn-cybersecurity-vlan-471
SUB-REQ-078 | All physical materials and surfaces within growing zones that contact nutrient solution, irrigation water, or air recirculation streams SHALL comply with FDA 21 CFR Part 174-186 (food contact materials) and SHALL be verified clean-in-place (CIP) compatible with 2% peracetic acid sanitisation solution at ambient temperature. | subsystem-requirements | Subsystem Requirements |  | Inspection | 86 |  | UHT classifies growing zones with the Biological/Biomimetic trait (bit 3) because zones contain live plant matter and microbiomes. Lint finding 7 flags the absence of biocompatibility or sterilisation requirements. Under FSMA (21 CFR Part 112), indoor growing facilities producing leafy greens for direct human consumption must demonstrate that materials contacting edible plant matter are food-safe. Peracetic acid is the standard sanitisant for hydroponic systems; CIP compatibility ensures the zone can be sanitised in place without disassembly, which is also required by SYS-REQ-016 (sanitisation sequence verification before new crop activation). | subsystem, zone-controller-network, food-safety, compliance, session-471, idempotency:sub-zone-biocompat-fda-471
SUB-REQ-079 | The Zone Climate Controller SHALL accept a supervisory override command from the Supervisory Control Subsystem within 2 seconds to either SUSPEND autonomous setpoint control (holding last actuator state) or SAFE-MODE (de-energise all HVAC actuators), and SHALL NOT resume autonomous operation until the Supervisory Control explicitly releases the override. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Lint finding: zone climate controller classified as Functionally Autonomous (bit 15) but had no supervisory override requirement. Autonomous control must yield to supervisory authority to prevent crop loss during fault conditions, prevent runaway control during sensor failure, and support orderly shutdown sequences. | idempotency:sub-zcc-override-qc472
SUB-REQ-080 | The Zone Controller Unit SHALL respond to a SUSPEND or SAFE-MODE override command from the Zone Edge Gateway within 500 ms by either freezing all setpoint outputs at current values or de-energising all zone actuator outputs, and SHALL transmit an acknowledgement back via OPC UA confirming the override state. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Lint finding: zone controller unit classified as Functionally Autonomous (bit 15) but lacked override constraints. The 500ms response time is required to coordinate with the safety interlock subsystem response chain; supervisory override is essential for controlled zone shutdowns without triggering interlock trips. | idempotency:sub-zcu-override-qc472
SUB-REQ-081 | The Zone Climate Controller SHALL operate from the zone control panel 24VDC supply rail with a maximum steady-state power draw not exceeding 15W per unit, and SHALL incorporate a local hold-up capacitor providing ≥200ms of brownout ride-through to prevent uncontrolled actuator state changes during supply voltage transients. | subsystem-requirements | Subsystem Requirements |  | Test | 86 |  | Lint finding: zone climate controller classified as Powered (bit 4) but had no power budget or supply requirement. The 15W limit constrains panel heat load for a standard 8-zone panel; 200ms ride-through aligns with UPS switchover time to prevent spurious actuator state changes. | idempotency:sub-zcc-power-qc472
SUB-REQ-082 | The Supervisory Control Subsystem SHALL be housed in an IEC 60529 IP54-rated 19-inch 4U rack-mount enclosure with front-panel LED indicators for system health, alarm, and communication status, suitable for installation in a climate-controlled control room at operating temperatures of +5 degC to +45 degC. | subsystem-requirements | Subsystem Requirements | ubiquitous | Inspection | 86 |  | The Supervisory Control Subsystem contains industrial compute hardware subject to dust and humidity ingress in a farm environment; IP54 rack-mount packaging ensures hardware longevity and maintainability. UHT classification confirms the component carries physical embodiment traits requiring explicit enclosure constraints. | idempotency:qc-phys-scs-enclosure-v1
SUB-REQ-083 | The Zone Controller SHALL be packaged as a DIN-rail-mounted embedded controller rated to IEC 60529 IP54, operating across -5 degC to +55 degC ambient, with dimensions not exceeding 140 mm W x 100 mm H x 60 mm D to fit within the zone control panel. | subsystem-requirements | Subsystem Requirements | ubiquitous | Inspection | 86 |  | Zone controllers are mounted inside wet, humid growing zones; IP54 DIN-rail packaging is the minimum protection level for continuous operation in this environment. Dimensional constraints are derived from the zone control panel enclosure design to ensure physical fitment. | idempotency:qc-phys-zc-enclosure-v1
SUB-REQ-084 | The Zone Controller Network cabling SHALL use shielded twisted-pair industrial Ethernet cable rated for continuous exposure to water splash and nutrient solution mist, with IP67-rated field junction boxes at each zone entry point, supporting network segments up to 100 m at 100 Mbps without active repeaters. | subsystem-requirements | Subsystem Requirements | ubiquitous | Inspection | 86 |  | Network cabling traversing the growing zone is exposed to condensation and nutrient spray; specifying shielded cable and IP67 junction boxes prevents corrosion-induced network faults that would disrupt closed-loop zone control. The 100 m segment limit is the Cat6A maximum for 100BASE-TX. | idempotency:qc-phys-zcn-cabling-v1
SUB-REQ-085 | The CO2 Enrichment Subsystem SHALL be housed in a ventilated, wall-mounted IEC 60529 IP54-rated steel enclosure located within 2 m of the CO2 supply manifold, incorporating integrated solenoid valve driver circuits and a 24 VDC power supply rated to supply all zone injection solenoids simultaneously at a maximum combined load of 20 A. | subsystem-requirements | Subsystem Requirements | ubiquitous | Inspection | 86 |  | Proximity mounting minimises CO2 supply piping runs and pressure drop; combined solenoid load rating prevents nuisance trips during simultaneous zone injection during peak crop growth periods. Ventilation prevents heat buildup from solenoid drivers. | idempotency:qc-phys-enrich-enclosure-v1
SUB-REQ-086 | The Zone Climate Controller SHALL be packaged in an IEC 60529 IP54 DIN-rail-mount enclosure with dedicated RS-485 Modbus RTU termination ports, an integral galvanically isolated 24 VDC power rail, and shall withstand sinusoidal vibration levels of 0.5 g RMS over 10-150 Hz for continuous operation in a fan-cooled equipment cabinet. | subsystem-requirements | Subsystem Requirements | ubiquitous | Test | 86 |  | Zone Climate Controllers are installed in equipment cabinets adjacent to HVAC plant; vibration from fan motors and compressors requires 0.5g RMS rating derived from ASHRAE guidelines for fan vibration in air handling units. Galvanic isolation on the 24V rail protects against ground-loop noise from large HVAC motors. | idempotency:qc-phys-zcc-enclosure-v1
SUB-REQ-087 | The CO2 Injection Controller SHALL be housed in a glass-reinforced polyester (GRP) enclosure rated to IEC 60529 IP65, mounted external to the growing zone, and SHALL incorporate a manual isolation valve interface and solenoid position indicator to support safe maintenance under lockout/tagout (LOTO) procedures per IEC 60204-1. | subsystem-requirements | Subsystem Requirements | ubiquitous | Inspection | 86 |  | GRP enclosures are preferred for CO2 equipment because they resist the HNO3-based condensation from nutrient misting without the galvanic corrosion risk of steel. External mounting enables LOTO access without entering the CO2-enriched zone, addressing a COSHH control requirement for CO2 service operations. | idempotency:qc-phys-co2ic-enclosure-v1
SUB-REQ-088 | All surfaces within a growing zone that are directly exposed to nutrient solution or crop root mass SHALL be constructed from food-safe, non-porous materials — specifically stainless steel grade 316L or HDPE — complying with FDA 21 CFR Part 177 to prevent pathogen harbouring and ensure biocompatibility with edible crops. | subsystem-requirements | Subsystem Requirements | ubiquitous | Inspection | 86 |  | Vertical farm zones grow edible produce; pathogen contamination from surface materials (e.g., biofilm formation on porous substrates) presents a direct food safety hazard. FDA 21 CFR Part 177 sets the material standard for food-contact surfaces, and 316L SS/HDPE are proven choices for nutrient solution contact in hydroponics, matching industry certification expectations for GAP compliance. | idempotency:qc-bio-zone-materials-v1
SUB-REQ-089 | While a growing zone is undergoing sanitation, the Zone Controller SHALL enforce a zone isolation interlock that prevents nutrient delivery and CO2 injection until a minimum 30-minute hypochlorous acid fog or UV-C irradiation sterilisation cycle has completed, confirmed by sensor-based cycle completion verification. | subsystem-requirements | Subsystem Requirements | state | Test | 86 |  | Inadequate sanitisation between crop cycles is the primary route for Fusarium and E. coli O157 entry into a hydroponic system; a mandatory 30-minute chemical or UV-C cycle is the minimum effective contact time per UK HSE hydroponics guidance. Zone isolation during sanitisation prevents nutrient contamination of cleaning agents and protects next-crop food safety. | idempotency:qc-bio-zone-sterilisation-v1
SUB-REQ-090 | The Zone Climate Controller SHALL be a physically-housed DIN-rail-mounted controller unit installed in zone electrical enclosures, with a housing conforming to IEC 60715 and rated to IEC 60529 IP20, operating at 24 VDC supply, within ambient temperature range -10 to +55 degC. | subsystem-requirements | Subsystem Requirements |  | Inspection | 86 |  | Zone Climate Controller executes PID loops for HVAC actuators and must be co-located with zone I/O in electrical enclosures. Physical housing specification ensures the unit is procurable as a mountable hardware LRU and integrates with the DIN-rail ecosystem. Without this, the controller is treated as a pure software module. | idempotency:sub-zone-climate-ctrl-housing-474
SUB-REQ-091 | The CO2 Injection Controller SHALL be a physically-housed controller unit installed in a GRP or 304 stainless steel enclosure rated to IEC 60529 IP54, DIN-rail or panel-mounted in plant-room equipment corridors outside growing zones, with analogue 4-20 mA I/O terminals and RS-485 Modbus RTU communications port, operating at 24 VDC supply within -10 to +50 degC ambient. | subsystem-requirements | Subsystem Requirements |  | Inspection | 86 |  | CO2 Injection Controller is a process control device handling pressurised gas at up to 10 bar and must be installed in a location accessible for maintenance without disturbing active crop cycles. IP54 protection is required for the agricultural plant-room environment with cleaning spray and humidity. Physical housing specification enables procurement as a hardware LRU and defines installation zone, which is a safety requirement given CO2 asphyxiation hazard. | idempotency:sub-co2-inject-ctrl-housing-474
SUB-REQ-092 | The Vertical Farm Environment Controller SHALL ensure that all sensors, actuators, and hardware installed within growing zones are constructed from food-safe, non-toxic, corrosion-resistant materials (stainless steel 304/316, food-grade ABS, or equivalent) and comply with biocompatibility requirements of EN 1186 or equivalent applicable food-contact material standard, to prevent contamination of crops or nutrient solution. | subsystem-requirements | Subsystem Requirements |  | Inspection | 86 |  | Vertical farm growing zones contain live crops intended for human consumption. All hardware co-located in zones with plants can leach trace materials into nutrient solution or onto crop surfaces. Stainless steel 304/316 and food-grade ABS are established food-safe materials. Biocompatibility certification prevents regulatory non-compliance with food safety legislation (e.g., EU Regulation 10/2011 on plastic materials in food contact) and protects consumer health. | idempotency:sub-zone-biocompat-474
SUB-REQ-094 | The Zone Controller SHALL be a physically-housed embedded controller unit with a DIN-rail-mounted enclosure rated to IEC 60529 IP20, installed in zone electrical enclosures adjacent to each growing zone, with RS-485 serial ports, 24 VDC power input, and digital I/O terminals, operating within ambient temperature -10 to +55 degC and humidity 20-95% RH non-condensing. | subsystem-requirements | Subsystem Requirements |  | Inspection | 86 |  | Zone Controllers are the local automation nodes executing real-time PID control. Physical housing in zone electrical enclosures is necessary for cable management, maintenance access, and compliance with IEC 61439 (low-voltage switchgear). The IP20 rating and temperature/humidity specification ensure suitability for the agricultural electrical enclosure environment. Without a physical housing requirement, zone controllers cannot be selected or installed as real hardware units. | idempotency:sub-zone-ctrl-housing-474
SUB-REQ-095 | The Zone Controller Network physical infrastructure SHALL comprise shielded twisted-pair industrial Ethernet cabling (minimum Cat5e, foil/braid shield) rated for continuous exposure to humidity and nutrient mist, IP67-rated GRP field junction boxes at each zone entry point, and 19-inch 1U managed industrial Ethernet switches installed in the Supervisory Control Subsystem enclosure, supporting network segments up to 100 m at 100 Mbps. | subsystem-requirements | Subsystem Requirements |  | Inspection |  |  | Zone Controller Network must specify its physical cabling infrastructure to ensure reliable communications in the high-humidity, nutrient-mist environment of the growing facility. Shielded cabling and IP67 junction boxes protect network hardware from corrosion and condensation. Without explicit physical infrastructure requirements, the network cannot be procured or installed as a real hardware system. Derived from ARC-REQ-002 distributed architecture decision and IFC-REQ-013, IFC-REQ-016 which impose physical routing and termination constraints. | idempotency:zcn-physical-infrastructure-v1
SUB-REQ-096 | All materials in direct contact with growing zone air, water, or growing media SHALL be food-safe, non-toxic, and resistant to degradation by peracetic acid (PAA) at concentrations up to 2000 ppm, sodium hypochlorite at 200 ppm, and pH ranges 2.0-10.0. Zone surfaces SHALL be cleanable to a surface bioburden below 100 CFU/cm2 after the standard sanitisation cycle. | subsystem-requirements | Subsystem Requirements |  | Test |  |  | Growing zones contain crops for human consumption; material biocompatibility and cleanability prevent contamination of produce with chemicals, heavy metals, or pathogens. Peracetic acid and hypochlorite concentrations reflect the standard sanitisation protocol used between crop cycles. The 100 CFU/cm2 bioburden limit is based on ISO 22000 food safety standard guidance for food-contact surfaces. Without these requirements, there is no baseline for material selection or sanitisation effectiveness qualification. | idempotency:zone-biocompatibility-v1
SUB-REQ-097 | When a harvest crew zone entry signal is received from a zone access control reader, the Vertical Farm Environment Controller SHALL within 60 seconds switch the zone to worker-comfort mode: set temperature setpoint to 22 degC, set white-channel LED intensity to 50% of current output, disable CO2 enrichment injection for the zone, and prevent automatic return to production recipe setpoints until a zone-clear signal is received from the same access control reader. | subsystem-requirements | Subsystem Requirements | event | Test |  |  | Derived from STK-REQ-008: harvest crew working in a zone face risks from elevated CO2 (>1000 ppm causes cognitive impairment, >5000 ppm is life-threatening), high-intensity grow lighting (>600 µmol/m2/s causes eye and skin damage), and sub-optimal temperature. Without an automatic worker-comfort mode, operators must manually reconfigure zone parameters before entry, increasing the risk of a crew member entering a zone with hazardous conditions. The 60-second response time is derived from the expected transit time from access control reader to the growing zone. This is a safety-critical operational mode: the system must not return to production conditions while crew are present. | idempotency:sys-worker-comfort-mode-477
SYS-REQ-001 | The Vertical Farm Environment Controller SHALL maintain zone temperature within ±1.0°C of crop recipe setpoint during Production Operation, with control loop response time not exceeding 120 seconds for a 2°C step disturbance. | system-requirements | System Requirements |  | Test | 100 |  | Derived from grower technician need for precise zone-specific climate control. ±1°C tolerance is the threshold below which leafy green growth rate variation remains within 5% of optimal. 120-second response to 2°C step prevents thermal accumulation that would trigger yield impact estimates. | rt-mechanical-trace, red-team-session-480
SYS-REQ-002 | The Vertical Farm Environment Controller SHALL maintain zone relative humidity within ±5% RH of crop recipe setpoint during Production Operation, and shall not permit humidity to exceed 90% RH in any zone to prevent condensation on LED fixtures and electronics. | system-requirements | System Requirements |  | Test | 86 |  | Derived from grower technician zone control need and physical environment constraint. ±5% RH is achievable with dehumidification control. 90% RH ceiling prevents condensation at the dew point difference present when zone air meets cooler electronic surfaces, avoiding H-002 electrocution hazard pathway. | system, climate, session-462, idempotency:sys-humidity-control-462
SYS-REQ-003 | The Vertical Farm Environment Controller SHALL regulate zone CO2 concentration within ±50 ppm of crop recipe setpoint during enrichment periods, and SHALL NOT permit CO2 concentration to exceed 3000 ppm under software control in any zone. | system-requirements | System Requirements |  | Test | 86 |  | Derived from grower technician recipe management and H-001 CO2 asphyxiation hazard. ±50ppm is achievable with NDIR sensors and proportional solenoid control. 3000ppm software ceiling provides margin below the 5000ppm OSHA TWA limit, with hardware interlock at 5000ppm as independent backup per SIL 3 allocation. | rt-mechanical-trace, red-team-session-480
SYS-REQ-004 | When zone CO2 concentration exceeds 5000 ppm as measured by the independent safety-rated CO2 sensor, the safety interlock subsystem SHALL de-energise all CO2 injection solenoid valves and activate emergency ventilation within 2 seconds, independent of the software controller. | system-requirements | System Requirements |  | Test | 86 |  | H-001 drives SIL 3: CO2 enrichment valve failure could cause lethal accumulation. Hardware interlock must operate independently of software controller to achieve SIL 3 integrity. 2-second response limits CO2 rise rate in enclosed zone volume. 5000ppm trigger is OSHA TWA limit. | rt-mechanical-trace, red-team-session-480
SYS-REQ-005 | The Vertical Farm Environment Controller SHALL control zone LED lighting intensity within ±5% of crop recipe PAR setpoint (range 100-600 µmol/m²/s) and execute photoperiod transitions (on/off ramps) over a configurable 5-30 minute ramp period. | system-requirements | System Requirements |  | Test | 100 |  | Derived from grower technician recipe adjustment need. ±5% PAR accuracy ensures consistent daily light integral (DLI) for crop quality. 5-30 minute ramp prevents thermal shock to LED drivers and avoids instantaneous 200kW load steps that would trigger demand charges. | system, lighting, session-462, idempotency:sys-lighting-control-462
SYS-REQ-006 | The Vertical Farm Environment Controller SHALL regulate nutrient solution pH within ±0.2 of crop recipe setpoint and EC within ±0.1 mS/cm of setpoint, with dosing pump stroke volume not exceeding 2% of tank volume per injection to prevent overshoot. | system-requirements | System Requirements |  | Test | 86 |  | Derived from grower technician nutrient management and H-003 chemical burn hazard. ±0.2 pH keeps nutrient availability within crop tolerance band. 2% stroke volume limit prevents pH overshoot that could drive tank below pH 2 from a single dose event, supporting the SIL 2 safe state requirement. | rt-mechanical-trace, red-team-session-480
SYS-REQ-007 | When pH dosing pump cumulative injection exceeds 5% of tank volume within any 10-minute window without pH reaching the target band, the Vertical Farm Environment Controller SHALL suspend dosing, alarm the operator, and log the event as a potential sensor drift condition. | system-requirements | System Requirements |  | Test | 86 |  | H-003 drives SIL 2: Runaway dosing from drifted sensor could produce dangerous acid/alkali concentrations. Cumulative volume limit detects sensor drift scenario from Nutrient Sensor Drift ConOps scenario. Suspension prevents tank reaching corrosive pH before operator intervention. | system, sil-2, safety, nutrient, session-462, idempotency:sys-dosing-protection-462
SYS-REQ-008 | When a zone HVAC compressor trips, the Vertical Farm Environment Controller SHALL automatically reduce LED power in the affected zone by at least 40% within 60 seconds and increase extraction fan speed to maximum, while compensating adjacent zone HVAC loads to maintain their setpoints. | system-requirements | System Requirements |  | Test | 86 |  | Derived from HVAC Failure scenario and H-004 thermal hazard. LED heat is the dominant internal load in growing zones; 40% LED reduction cuts thermal input by approximately 40kW per zone, buying 2-4 hours before temperature exceeds crop damage threshold. Adjacent zone compensation prevents cascading degradation. | system, sil-2, degraded, session-462, idempotency:sys-hvac-degraded-462
SYS-REQ-009 | When LED fixture surface temperature exceeds 85°C or zone temperature exceeds 38°C, the Vertical Farm Environment Controller SHALL de-energise affected LED circuits within 5 seconds to prevent thermal runaway. | system-requirements | System Requirements |  | Test | 100 |  | H-004 drives SIL 2: HVAC failure combined with high-power LED operation creates thermal runaway risk. 85°C fixture temperature is 15°C below typical LED driver thermal shutdown. 38°C zone temperature provides margin below 45°C crop destruction and fire risk threshold. | system, sil-2, safety, session-462, idempotency:sys-thermal-protection-462
SYS-REQ-010 | The Vertical Farm Environment Controller SHALL detect irrigation valve stuck-open conditions within 30 seconds using flow meter feedback and close the upstream zone isolation valve, activating floor-level drain pumps within 60 seconds. | system-requirements | System Requirements |  | Test | 100 |  | H-005 drives SIL 2: Uncontrolled water release in a multi-storey structure risks structural overload and electrical shorts on lower floors. 30-second detection window limits water volume to approximately 50 litres at typical irrigation flow rates, within floor drain capacity. | system, sil-2, safety, session-462, idempotency:sys-water-leak-462
SYS-REQ-011 | The Vertical Farm Environment Controller SHALL log all environmental parameters (temperature, humidity, CO2, PAR, pH, EC, flow rates) at minimum 1-minute intervals per zone with UTC timestamps, cryptographic integrity verification, and local storage capacity for minimum 90 days of full-resolution data. | system-requirements | System Requirements |  | Test | 86 |  | Derived from STK-REQ-009 (auditor log integrity) and STK-REQ-010 (HACCP-compliant deviation reports). Cryptographic signing (tamper-evident) requires Test: the signing mechanism must be exercised and a tampered log entry must be rejected. The 2-year retention requirement requires Test: sustained logging at 1-minute intervals per zone must be verified under realistic data volume to confirm retention policy enforcement. Inspection of code or specification alone cannot confirm correct crypto verification behaviour or that old records are not silently dropped when storage fills. | rt-mechanical-trace, red-team-session-480
SYS-REQ-012 | The Vertical Farm Environment Controller SHALL respond to OpenADR 2.0 demand-response events by executing a pre-configured load curtailment profile within 5 minutes, reducing facility electrical demand by at least 30% while maintaining zone temperatures within 4°C of setpoint and CO2 within safe limits. | system-requirements | System Requirements |  | Test | 86 |  | Derived from energy utility demand response need. 30% curtailment from 1MW baseline saves approximately £150/event in avoided demand charges at UK industrial tariffs. 4°C temperature relaxation is the maximum short-duration excursion that does not trigger yield impact for leafy greens. | system, energy, session-462, idempotency:sys-demand-response-462
SYS-REQ-013 | The Vertical Farm Environment Controller SHALL execute the emergency shutdown sequence (CO2 valve closure, emergency ventilation, non-essential load de-energisation) within 3 seconds of any safety interlock trigger, and SHALL require two-person reset (physical key plus software acknowledgement) before returning to Production Operation. | system-requirements | System Requirements |  | Test | 86 |  | Derived from CO2 Leak Emergency scenario and harvest crew safety need. 3-second total sequence time limits CO2 accumulation. Two-person reset prevents premature restart before hazard is verified cleared, aligning with IEC 62061 requirements for safety function reset. | system, sil-3, safety, session-462, idempotency:sys-emergency-shutdown-462
SYS-REQ-014 | The Vertical Farm Environment Controller SHALL isolate zone airflow (HVAC dampers closed) and nutrient recirculation when pathogen contamination is detected or suspected, and SHALL activate UV sterilisation on affected nutrient lines within 5 minutes. | system-requirements | System Requirements |  | Test | 100 |  | H-006 drives SIL 1: Uncontrolled pathogen spread between zones via shared air or nutrient systems causes multi-zone crop loss and food safety risk. Airflow isolation prevents aerosol transmission. Nutrient isolation prevents waterborne pathogen spread. UV treatment inactivates common hydroponic pathogens (Pythium, Fusarium). | system, sil-1, biosecurity, session-462, idempotency:sys-pathogen-isolation-462
SYS-REQ-015 | The Vertical Farm Environment Controller safety-critical control functions (CO2 interlock, thermal protection, water leak detection) SHALL be implemented on hardware independent of the supervisory software controller, with a mean time to dangerous failure (MTTFd) of at least 150 years per safety function. | system-requirements | System Requirements |  | Test | 86 |  | IEC 61508 SIL-3 requires that hardware independence of the safety system be demonstrated, not merely analysed. The independence claim — that supervisory software failure cannot affect the safety PLC — must be demonstrated by: (1) crashing the supervisory software while the Safety PLC is executing interlock logic, and confirming no interlock state change occurs; (2) disconnecting the data-diode network path and confirming the Safety PLC continues normal operation. Analysis of the architecture alone cannot confirm there are no undocumented shared resources (power rails, communication buses, or firmware update paths) between the supervisory system and the SIL-3 Safety PLC. | rt-mechanical-trace, red-team-session-480
SYS-REQ-016 | The Vertical Farm Environment Controller SHALL complete zone sanitisation sequence verification (peracetic acid contact time, rinse water pH/EC confirmation, drain completion) before permitting new crop recipe activation, blocking germination phase until all verification criteria pass. | system-requirements | System Requirements |  | Demonstration | 100 |  | Derived from Crop Changeover scenario: Sanitisation chemical residue on new crop is a food safety risk. EC/pH sensors verify rinse completeness. Blocking germination phase prevents planting into contaminated media, which would result in crop loss and potential food safety violation. | system, compliance, changeover, session-462, idempotency:sys-sanitation-verify-462
SYS-REQ-017 | When the primary Vertical Farm Environment Controller processing node fails, the system SHALL restore zone regulation functions (temperature, CO2, pH, and lighting) from a warm-standby node within 30 seconds, with no more than one missed control cycle per zone. | system-requirements | System Requirements | event | Test | 86 |  | UHT classifies the vertical farm environment controller (D1F77818) as System-Essential (bit 16). A single point of failure at the top-level controller results in simultaneous loss of all environmental regulation across all zones, risking crop loss within hours for temperature-sensitive cultivars. | idempotency:qc-468-vfec-redundancy
SYS-REQ-018 | The Vertical Farm Environment Controller SHALL provide a supervisory HMI displaying real-time zone status (temperature, humidity, CO2, pH, lighting intensity) with alert acknowledgement within 3 user interactions, accessible from any network-connected browser without additional software installation. | system-requirements | System Requirements | ubiquitous | Demonstration | 86 |  | STK-REQ-002 identifies farm operators as needing a system that allows easy monitoring and adjustment. The 3-interaction acknowledgement limit and browser-native access derive from operator usability research for industrial HMI: operators wearing gloves or using shared terminals need minimal click-through paths. | idempotency:qc-468-hmi-sys-req
SYS-REQ-019 | The Vertical Farm Environment Controller SHALL comply with IEC 61000-4 series immunity standards (surge, EFT, ESD, conducted, and radiated) at immunity test levels specified by IEC 61000-6-2 for industrial environments. | system-requirements | System Requirements | ubiquitous | Test | 86 |  | Vertical farm controllers operate in an electrically noisy industrial environment with variable-speed drives, switching power supplies, and CO2 solenoid valves generating conducted and radiated emissions. IEC 61000-6-2 sets the industrial immunity benchmark; compliance ensures the controller does not misread sensor data or fail to execute safety shutdowns during EMC disturbances. | idempotency:qc-468-emc-sys-req
SYS-REQ-020 | The Vertical Farm Environment Controller SHALL store a minimum of 200 crop recipes and their associated control parameters in local non-volatile storage and SHALL continue autonomous zone regulation from stored recipes for a minimum of 72 hours following loss of network connectivity to external systems. | system-requirements | System Requirements | ubiquitous | Test | 86 |  | STK-REQ-016 requires locally stored crop recipes and control parameters. The 200-recipe minimum covers expected commercial cultivar variety. The 72-hour autonomous operation target derives from worst-case ISP outage duration at rural agricultural sites where fibre restoration typically takes 24-48 hours. | idempotency:qc-468-local-storage-sys-req
VER-REQ-001 | Verify IFC-REQ-006: With three CO2 sensor channels connected to the Safety PLC, inject calibrated CO2 concentration levels at 0 ppm, 2500 ppm, 5000 ppm, and 9900 ppm on each channel independently; confirm PLC analog input readings match injected values within ±50 ppm. Simulate wire-open on each channel individually; confirm PLC raises sensor-fault alarm within 1s and does not interpret the failure as 0 ppm CO2. PASS: all readings within tolerance, all wire-break faults detected. | verification-requirements | Verification Requirements |  | Test | 57 |  | Integration test to verify interface compliance at system boundaries. | verification, safety-interlock, sil-3, session-463, idempotency:ver-ifc006-463
VER-REQ-002 | Verify IFC-REQ-007: With the Safety PLC in test mode, de-energise each relay coil output in sequence; confirm the corresponding final element moves to its safe state within 500 ms. Open-circuit each relay coil wire in turn; confirm wire-break fault is raised by the PLC within 1s and the relay de-energises. PASS: all final elements reach safe state on demand, all wire-break faults detected. | verification-requirements | Verification Requirements |  | Test | 57 |  | Integration test to verify interface compliance at system boundaries. | verification, safety-interlock, sil-3, session-463, idempotency:ver-ifc007-463
VER-REQ-003 | Verify SUB-REQ-005 (end-to-end integration): In a commissioned zone with live sensors, inject CO2 test gas at 5100 ppm to safety sensor channels; measure time from injection stabilisation to CO2 isolation valve fully-closed position; confirm ≤30s. Repeat for LED thermal (heat gun to >85°C, confirm LED circuit breaker OPEN ≤10s) and emergency-stop button (confirm all zone outputs de-energised ≤1s). PASS: all measured response times within specified limits with audit log entry created. | verification-requirements | Verification Requirements |  | Test | 57 |  | End-to-end test covering the complete signal path from sensor through Safety PLC, Voted Logic Engine, and Hardwired Trip Bus to final elements. Tests the composite requirement that each interlock acts within the hazard-specific time window. This is the primary safety case evidence for SIL 3 functional verification of the CO2 and thermal interlocks. | verification, safety-interlock, sil-3, session-463, idempotency:ver-sub005-e2e-463
VER-REQ-004 | Verify SUB-REQ-001: Expose three CO2 Safety Sensor Array channels to NIST-traceable calibration gas at 0, 1000, 2500, 5000, and 9000 ppm; record each channel reading; confirm deviation ≤50 ppm at each point. Verify SIL 3 certification documentation for sensor type. PASS: all readings within ±50 ppm, SIL 3 certificate present. | verification-requirements | Verification Requirements |  | Test | 57 |  | Accuracy verification at multiple concentration points spanning the operational range (1000-2000 ppm normal, 5000 ppm trip threshold). NIST-traceable calibration gas provides metrological traceability for the safety case. | verification, safety-interlock, sil-3, session-463, idempotency:ver-sub001-accuracy-463
VER-REQ-005 | Verify IFC-REQ-014, IFC-REQ-018, IFC-REQ-019: With the Safety PLC in test mode, inject CO2 over-threshold, zone temperature over-threshold (38°C), and dosing-excess signals simultaneously via the hardwired input channels. Confirm that each signal propagates to the PLC input register within the specified latency (500ms, 100ms, 200ms respectively) using a calibrated signal logger, and that each triggers the correct safe-state actuation. | verification-requirements | Verification Requirements | ubiquitous | Test | 57 |  | Three hardwired interface requirements specify independent safety input channels. Testing them in a combined injection scenario verifies that no channel interferes with another and that the voted logic engine correctly processes simultaneous multi-hazard inputs, matching the SIL 3 diagnostic requirement. | idempotency:ver-hardwired-inputs-464
VER-REQ-006 | Verify IFC-REQ-009, IFC-REQ-010, IFC-REQ-011, IFC-REQ-012, IFC-REQ-013: In a factory acceptance test environment with all subsystem controllers connected to a test zone controller network, inject recipe parameter changes and confirm propagation latency for each interface is within specification. Verify EC/pH feedback accuracy (±0.1 mS/cm, ±0.05 pH) using calibrated reference instruments. | verification-requirements | Verification Requirements | ubiquitous | Test | 57 |  | Process network interfaces between supervisory control, climate, nutrient, and lighting subsystems share the same Modbus TCP/IP backbone. FAT in integrated configuration verifies that simultaneous traffic from all subsystems does not degrade the latency of any individual interface below its specified bound. | idempotency:ver-process-network-ifc-464
VER-REQ-007 | Verify IFC-REQ-022: connect Zone NDIR CO2 Sensor Array analogue output (4-20mA) to CO2 Injection Controller input; inject calibrated current at 4mA (sensor fail), 8mA (600 ppm), 12mA (1200 ppm), 16mA (1800 ppm), 20mA (2400 ppm); confirm controller readings within ±50 ppm of expected; simulate open-circuit (<3.6mA) and confirm fault alarm within 5 seconds; PASS: all readings within tolerance, open-circuit detected. | verification-requirements | Verification Requirements |  | Test | 57 |  | Interface test verifying 4-20mA signal calibration scaling and open-circuit fault detection, both required for correct PID operation and sensor fault safety behaviour. | verification, co2-enrichment-subsystem, session-465, idempotency:ver-ifc022-465
VER-REQ-008 | Verify IFC-REQ-023: command zone solenoid valve to open via CO2 Injection Controller 24VDC output; confirm position feedback indicates open within 2 seconds; command valve to close; confirm position feedback indicates closed within 500 ms; force open/close command mismatch by mechanically jamming valve and verify CO2 Injection Controller raises valve-fault alarm within 2 seconds; PASS: all timings within specification, fault alarm raised. | verification-requirements | Verification Requirements |  | Test | 57 |  | Valve command/feedback interface test covering both normal operation timing and fault detection, which is the primary mechanism for detecting valve seizure in process operation. | verification, co2-enrichment-subsystem, session-465, idempotency:ver-ifc023-465
VER-REQ-009 | Verify CO2 Enrichment Subsystem end-to-end (system integration test): with all subsystems connected in a live test environment, command a zone CO2 setpoint from 400 ppm to 1000 ppm via Supervisory Control; measure time to achieve 1000 ppm ±50 ppm; inject simulated 5000 ppm safety sensor reading and verify all zone solenoid valves close within 2 seconds and CO2 Injection Controller enters lockout; PASS: setpoint achieved within 5 minutes, trip response ≤2 seconds under nominal load. | verification-requirements | Verification Requirements |  | Test | 57 |  | End-to-end integration test exercising the complete chain from supervisory setpoint through injection control to physical valve actuation, and the complete safety trip path from sensor reading through hardwired trip to valve closure. This is the primary evidence for SYS-REQ-003 and SYS-REQ-004 system-level verification. | verification, co2-enrichment-subsystem, session-465, sil-3, idempotency:ver-co2-e2e-465
VER-REQ-010 | Verify IFC-REQ-025: Configure Modbus RTU RS-485 at 9600 baud between EC/pH Sensor Array and Irrigation Controller. Confirm EC register value within ±0.1 mS/cm of reference meter at three setpoints (0.5, 3.0, 8.0 mS/cm). Confirm pH register value within ±0.05 of reference calibration buffer (pH 4.0, 7.0, 9.0). Set sensor to fault mode; confirm fault status register is set and Irrigation Controller logs fault within 5 seconds. Pass: all values within tolerance, fault detected within 5s. | verification-requirements | Verification Requirements |  | Test | 57 |  | Integration test verifying the Modbus RTU communication accuracy and fault reporting path required by IFC-REQ-025 and SUB-REQ-025, to confirm that sensor faults propagate before dosing can proceed on stale data. | verification, nutrient-management-subsystem, session-466, idempotency:ver-ifc025-466
VER-REQ-011 | Verify IFC-REQ-027: Command zone irrigation valve to open via Irrigation Controller 24VAC output; confirm reed-switch position feedback indicates open within 2 seconds. Command valve to close; confirm position feedback closed within 2 seconds. Mechanically restrain valve in open position, command close, and confirm Irrigation Controller reports stuck-valve fault to Zone Controller Network within 30 seconds. Pass: all timings within specification, stuck-valve fault detected and reported. | verification-requirements | Verification Requirements |  | Test | 57 |  | Interface test verifying both the 24VAC actuation path and position feedback confirmation, and the stuck-valve detection behaviour specified in SUB-REQ-030 and IFC-REQ-027. This test provides evidence that flood prevention response meets the 30-second detection window in SYS-REQ-010. | verification, nutrient-management-subsystem, sil-2, session-466, idempotency:ver-ifc027-466
VER-REQ-012 | Verify SUB-REQ-027 (Dosing Pump Array hardwired watchdog): Command a series of pH-down pump injections totalling 4.5% of tank volume in 8 minutes; confirm no fault contact assertion. Continue to 5.1% in the 10-minute window; confirm 24VDC fault contact asserts to Safety PLC within 200 ms of threshold crossing (measured with calibrated signal logger). Command pump operation while fault contact is asserted and confirm pumps are inhibited. Perform manual interlock reset and confirm pumps can resume. Pass: threshold detection within 200ms, pump inhibit enforced, manual reset required. | verification-requirements | Verification Requirements |  | Test | 43 |  | SIL-2 functional safety test for the dosing-excess watchdog required by SUB-REQ-027 and SYS-REQ-007. The 200ms signal propagation time is the primary safety timing requirement for this function. Testing both below-threshold (no spurious trip) and above-threshold (confirmed trip) scenarios validates the correct implementation boundary. Manual reset requirement is evidence of SIL-2 latched-trip behaviour. | verification, nutrient-management-subsystem, sil-2, safety, session-466, idempotency:ver-sub027-watchdog-466
VER-REQ-013 | Verify Nutrient Management Subsystem end-to-end (system integration test): with all NMS components connected in a live test environment, set zone recipe to pH 6.0/EC 2.5 mS/cm; confirm closed-loop dosing achieves setpoint within ±0.2 pH and ±0.1 mS/cm within 30 minutes; simulate stuck-open irrigation valve and confirm floor drain pump activates within 60 seconds; simulate sensor fault and confirm degraded-mode (SUB-REQ-037) operation at 50% dosing rate; simulate loss of mains power and confirm all zone valves close within 2 seconds. Pass: all system-level requirements met under combined conditions. | verification-requirements | Verification Requirements |  | Test | 57 |  | End-to-end integration test exercising the complete NMS signal chain from EC/pH feedback through dosing control to solution delivery, and the three primary fault responses: flood detection (SYS-REQ-010), sensor degraded mode (SUB-REQ-037), and power-loss fail-safe (SUB-REQ-032). This provides the primary evidence for SYS-REQ-006 and SYS-REQ-010 system-level verification. | verification, nutrient-management-subsystem, sil-2, session-466, idempotency:ver-nms-e2e-466
VER-REQ-014 | Verify SUB-REQ-039: In a commissioned zone with the PAR Sensor Array and LED Fixture Array installed at operating height, command the LCU to four PAR setpoints (100, 250, 400, 600 µmol/m²/s). At each setpoint under steady state (30s settled), measure PPFD with a calibrated reference quantum sensor at 9 canopy-level positions. Pass criterion: all 9 readings within ±5% of the commanded setpoint. | verification-requirements | Verification Requirements |  | Test | 57 |  | Multi-point canopy measurement with an independently calibrated reference sensor verifies both LCU closed-loop accuracy and spatial uniformity — the two failure modes that would cause recipe non-compliance. | verification, horticultural-lighting, session-467, idempotency:ver-sub039-par-accuracy-467
VER-REQ-015 | Verify SUB-REQ-042: In a test rig with a zone LED Driver Module Array energised and the Fixture Thermal Monitoring Array comparator circuit connected, inject a calibrated voltage equivalent to the 85 degree C threshold into the comparator input while monitoring Driver Module output current. Pass criterion: all Driver Module outputs de-energise within 2 seconds of threshold crossing, with no software intervention. Repeat 10 times. All 10 must pass. | verification-requirements | Verification Requirements |  | Test | 57 |  | SIL-2 functions require demonstrated probabilistic reliability — 10 consecutive trigger tests with zero failures provides minimum evidence for the diagnostic coverage claim. Hardware-only test path (no software intervention) directly verifies the SIL-2 architectural requirement. | verification, horticultural-lighting, sil-2, session-467, idempotency:ver-sub042-thermal-trip-467
VER-REQ-016 | Verify IFC-REQ-029: Using a DALI-2 bus analyser, command all four channel addresses to 10%, 50%, and 100% level. Measure round-trip command latency and verify driver status response received. Pass criterion: all responses received within 22 ms, all channels achieve commanded level within ±1 count, and no bus fault messages observed during 100-command test sequence. | verification-requirements | Verification Requirements |  | Test | 57 |  | Bus analyser verification of DALI-2 timing and addressing confirms IEC 62386 compliance and the 22ms response budget; 100-command sequence provides statistical confidence in error rate. | verification, horticultural-lighting, session-467, idempotency:ver-ifc029-dali-interface-467
VER-REQ-017 | Verify IFC-REQ-031: With the Fixture Thermal Monitoring Array trip bus connected to the Safety Interlock hardwired trip input, simulate open-circuit, short-to-ground, and threshold-crossing failure modes on the 24VDC line. Pass criterion: (a) open circuit triggers safety trip within 2s; (b) short to ground triggers safety trip within 2s; (c) threshold-crossing triggers safety trip within 2s. All three fault modes must activate the normally-closed trip correctly. | verification-requirements | Verification Requirements |  | Test | 57 |  | Three-fault-mode test verifies the fail-safe (normally-closed) behaviour of the SIL-2 interface — the key property that ensures wiring faults result in safe trips rather than missed trips. | verification, horticultural-lighting, sil-2, session-467, idempotency:ver-ifc031-thermal-hardwired-467
VER-REQ-018 | Verify SUB-REQ-012: inject test CO2 setpoint steps of 200 ppm across all zones simultaneously; measure controller response time and steady-state error over 30-minute test window; pass criterion: all zones achieve ±50 ppm of setpoint within 5 minutes of step and maintain within ±50 ppm for remainder. | verification-requirements | Verification Requirements |  | Test | 57 |  | Functional test of PID control performance under realistic multi-zone load, measuring both response time and steady-state accuracy against the ±50 ppm specification. | verification, co2-enrichment-subsystem, session-465, idempotency:ver-sub012-465
VER-REQ-019 | Verify SUB-REQ-017: de-energise zone solenoid valve from fully-open state and measure time to full closure via position feedback; test at 0°C, 20°C, and 40°C ambient; pass criterion: closure ≤500 ms at all temperatures with zero spring-return failures across 10 cycles per zone. | verification-requirements | Verification Requirements |  | Test | 57 |  | Valve closure time is safety-critical (SIL-3 trip budget allocation); tests must span the full operating temperature range since spring force and coil impedance vary with temperature. 10-cycle repeat confirms repeatability, not just one-off performance. | verification, co2-enrichment-subsystem, session-465, sil-3, idempotency:ver-sub017-465
VER-REQ-020 | Verify SUB-REQ-022: simulate safety interlock trip by removing 24VDC trip relay signal; verify all zone valves close within 500 ms via position feedback; verify CO2 Injection Controller enters lockout (refuses valve-open commands); attempt operator reset without authorised credential and verify lockout maintained; perform authorised reset and verify valves can re-open; pass criterion: all closure and lockout behaviours as specified, with valve closure time measured ≤500 ms. | verification-requirements | Verification Requirements |  | Test | 43 |  | SIL-3 safe state test must verify both the hardware trip mechanism (hardwired relay) and the software lockout behaviour, and must confirm that unauthorised reset is rejected. This is a mandatory SIL-3 functional safety test per IEC 61508-2. | verification, co2-enrichment-subsystem, session-465, sil-3, idempotency:ver-sub022-465
VER-REQ-021 | Verify REQ-SEVERTICALFARMENV-007: assert supervisory override command from simulated Supervisory Control Subsystem and measure elapsed time from command issuance to full actuator handover; pass criterion ≤500 ms in 10/10 trials. | verification-requirements | Verification Requirements | ubiquitous | Test | 71 |  | Tests the quantified 500 ms override response window for the zone controller network autonomy override requirement. Ten-trial pass rate confirms repeatability under varied network load conditions. | idempotency:qc-468-ver-zone-ctrl-override
VER-REQ-022 | Verify REQ-SEVERTICALFARMENV-008: kill primary VFEC processing node (power removal) while all zones active; measure time from node loss to full zone regulation resume from warm-standby; pass criterion ≤30 s with no more than 1 missed control cycle per zone. | verification-requirements | Verification Requirements | ubiquitous | Test | 57 |  | Directly tests the 30-second failover criterion and single-missed-cycle constraint. Power removal is chosen over software kill to test hardware-level failure detection. | idempotency:qc-468-ver-vfec-redundancy
VER-REQ-023 | Verify REQ-SEVERTICALFARMENV-011: attempt HMI login with valid username/password only (no OTP) and verify access is denied; verify TLS connection using protocol analyser to confirm TLS 1.3 negotiation and absence of plaintext credential transmission. | verification-requirements | Verification Requirements | ubiquitous | Test | 71 |  | Two-part test covers both authentication factor enforcement and transport encryption. Protocol analyser confirmation is required because browser UI success does not prove TLS version negotiated. | idempotency:qc-468-ver-cybersec
VER-REQ-024 | Verify SUB-REQ-053: In a commissioned grow zone with temperature setpoint 22 degC and full crop canopy, record zone air temperature at both PT100 sensor positions over a 4-hour steady-state period using a calibrated reference thermometer. Pass criterion: all readings within 22 ±1.0 degC with no outliers exceeding ±1.5 degC. | verification-requirements | Verification Requirements |  | Test | 57 |  | Zone-level steady-state test with reference thermometer provides independent calibration-traceable verification of the ±1.0 degC requirement; 4-hour window captures natural HVAC on/off cycling behaviour. | verification, climate-management, session-469, idempotency:ver-sub053-469
VER-REQ-025 | Verify SUB-REQ-055: Inject a simulated compressor trip signal at the HVAC Actuator Interface test port while the zone is at steady-state cooling. Measure time from trip signal injection to lighting load-reduction command on the Supervisory Control Subsystem interface using a logic analyser. Pass criterion: command issued within 500 ms on 10 consecutive trials with no failures. | verification-requirements | Verification Requirements |  | Test | 57 |  | Timing test with logic analyser provides objective, repeatable measurement of the 500 ms response requirement. Ten trials is the minimum statistical sample for a pass/fail safety function test per IEC 61511-1 clause 8.2. | verification, climate-management, session-469, idempotency:ver-sub055-469
VER-REQ-026 | Verify IFC-REQ-032: Connect a Modbus RTU bus analyser to the PT100 multiplexer bus and capture 1000 consecutive measurement frames. Pass criterion: all frames arrive within 1000 ±50 ms intervals; bus fault injection (open-circuit on one sensor) is detected and reported within one measurement cycle. | verification-requirements | Verification Requirements |  | Test | 57 |  | Protocol-level verification confirms the timing and fault-detection requirements of the interface. 1000 frames provides statistical confidence in 1 Hz compliance; fault injection test directly exercises the safety-relevant bus fault detection path. | verification, climate-management, session-469, idempotency:ver-ifc032-469
VER-REQ-027 | Verify IFC-REQ-034: Using a Modbus TCP test client, monitor the exchange between Fresh Air Ventilation Controller and CO2 Enrichment Subsystem for 30 minutes during steady-state production operation. Measure message interval and round-trip latency for all CO2 concentration and fresh-air fraction exchanges. Pass criterion: all message intervals within 2000 ±200 ms; all round-trip latencies below 200 ms. | verification-requirements | Verification Requirements |  | Test | 57 |  | Integration test captures the real-time exchange behaviour under operational conditions. 30-minute window spans multiple HRV damper adjustment cycles to verify steady-state interface compliance. | verification, climate-management, session-469, idempotency:ver-ifc034-469
VER-REQ-028 | Verify SUB-REQ-062: Trigger emergency shutdown by asserting the manual E-stop input while the facility is in full operation (all zones active, CO2 enrichment running). Use a multi-channel data logger to timestamp CO2 valve closure, nutrient pump stop, lighting kill, and HVAC damper purge signals. Pass criterion: complete sequence logged within 10 s from E-stop assertion on 3 consecutive trials. | verification-requirements | Verification Requirements |  | Test | 57 |  | End-to-end timing test with data logger provides objective evidence of the 10 s sequence requirement. Three trials at full-operation state are the minimum required to detect sequencing failures due to bus congestion or lock contention. | verification, supervisory-control, session-469, idempotency:ver-sub062-469
VER-REQ-029 | Verify IFC-REQ-036: Using an oscilloscope, measure propagation delay from Emergency Shutdown Sequencer 24V output assertion to Safety Interlock Subsystem input detection for each of the four shutdown signal lines. Pass criterion: all four lines show propagation delay less than 20 ms across 10 trials per line. | verification-requirements | Verification Requirements |  | Test | 57 |  | Oscilloscope measurement is the only method that can resolve sub-millisecond timing on the hardwired safety interface; functional test alone cannot verify the 20 ms latency bound specified in IFC-REQ-036. | verification, supervisory-control, session-469, idempotency:ver-ifc036-469
VER-REQ-030 | Verify IFC-REQ-037: Configure a test ZCU and Zone Edge Gateway on an isolated network, inject a known-value data set, and measure OPC-UA message round-trip latency over 1000 cycles under 100% data-change rate. Pass criteria: all messages use SignAndEncrypt, mean latency ≤100ms, 99th-percentile latency ≤150ms, no plaintext sessions accepted. | verification-requirements | Verification Requirements |  | Test | 57 |  | Integration test at the OPC-UA stack level verifies both functional (latency) and security (encryption) requirements simultaneously. 1000-cycle sample provides statistical confidence in the 99th-percentile measurement. | verification, zone-controller-network, session-470, idempotency:ver-ifc037-zcn-470
VER-REQ-031 | Verify IFC-REQ-038: Connect a ZCU to 4 I/O Expansion Modules on a single RS-485 segment and run a 24-hour polling cycle test at the specified baud rate. Inject an open-circuit fault on one analog channel. Pass criteria: complete scan cycle ≤250ms for all 4 modules, open-circuit fault detected and reported to ZCU within 1s, no scan cycle exceeds 500ms over 24 hours. | verification-requirements | Verification Requirements |  | Test | 57 |  | 24-hour continuous test catches intermittent timing violations under temperature cycling. The open-circuit injection directly tests the fault detection path of SUB-REQ-068. | verification, zone-controller-network, session-470, idempotency:ver-ifc038-zcn-470
VER-REQ-032 | Verify IFC-REQ-039: Audit the Ethernet switch configuration via SNMP MIB and running-config export. Verify VLAN 100 and VLAN 200 membership assignments. Attempt to send a unicast frame from VLAN 100 to a VLAN 200 host and confirm the frame is dropped at the switch. Pass criteria: VLAN membership matches design, zero VLAN 100 frames appear on VLAN 200 network monitor after 1000 test frames sent. | verification-requirements | Verification Requirements |  | Inspection | 57 |  | Configuration audit and active probe test verifies both the intended VLAN design and that the switch is enforcing it. A negative test (attempting to inject cross-VLAN traffic) is more rigorous than a positive-only test for a security isolation requirement. | verification, zone-controller-network, session-470, idempotency:ver-ifc039-zcn-470
VER-REQ-033 | Verify SUB-REQ-065: In a hardware-in-the-loop test, establish steady-state ZCU operation with known setpoints, then physically disconnect the OPC-UA network interface. Monitor zone parameter control over 35 minutes. Pass criteria: zone parameters remain within crop recipe tolerances for the full 35-minute test period, ZCU generates network-loss alarm within 60s of disconnect, control resumes on the stored local recipe when network is restored. | verification-requirements | Verification Requirements |  | Test | 57 |  | Hardware-in-the-loop test with actual ZCU hardware and simulated zone loads verifies autonomous operation in conditions representative of deployment. 35-minute test exceeds the 30-minute requirement to demonstrate margin. | verification, zone-controller-network, session-470, idempotency:ver-sub065-zcn-470
VER-REQ-034 | Verify SUB-REQ-070 and SUB-REQ-071: Inject 100,000 sensor data points at 1Hz into the TSDB from a simulated Zone Edge Gateway across 12 channels. Verify zero data loss in the raw store. Then execute a CSV export query for a 90-day range. Pass criteria: all 100,000 records present in TSDB, CSV export completes in ≤30 seconds, CSV row count matches injected count within 0.001% tolerance. | verification-requirements | Verification Requirements |  | Test | 57 |  | Combined test exercises both ingestion fidelity (SUB-REQ-070) and query performance (SUB-REQ-071) in a single dataset, confirming that the TSDB can sustain high-frequency writes without index degradation that would slow exports. | verification, data-acquisition, session-470, idempotency:ver-dac-tsdb-ingest-export-470
VER-REQ-035 | Verify SUB-REQ-072 and IFC-REQ-042: Connect the OpenADR VEN to a certified OpenADR 2.0b test VTN. Distribute 10 DR events at random intervals over 4 hours. Timestamp acknowledgements at VTN and curtailment commands at Supervisory message queue. Pass criteria: all 10 events acknowledged within 30 seconds, all 10 curtailment commands delivered to Supervisory queue within 35 seconds of event distribution. | verification-requirements | Verification Requirements |  | Test | 57 |  | End-to-end timing test using a certified test VTN verifies real protocol behaviour including HTTPS handshake overhead. Testing 10 events over 4 hours captures variation in network load conditions. | verification, data-acquisition, session-470, idempotency:ver-dac-oadr-timing-470
VER-REQ-036 | Verify SUB-REQ-074: Pre-populate the TSDB with a synthetic 4-hour sanitisation cycle dataset including peracetic acid concentration, temperature, and contact time telemetry. Trigger a compliance report generation event. Measure report generation time and verify SHA-256 hash. Pass criteria: PDF report generated within 60 seconds, report includes correct sanitisation parameters, SHA-256 hash of report matches hash of source TSDB records, hash is embedded in report metadata. | verification-requirements | Verification Requirements |  | Test | 57 |  | Synthetic dataset allows deterministic verification of report content and hash validity. The hash verification step confirms cryptographic linkage between report and source data, which is the key tamper-evidence property. | verification, data-acquisition, session-470, idempotency:ver-dac-compliance-report-470
VER-REQ-037 | Verify IFC-REQ-001 (BACnet/IP BMS interface): Connect the Vertical Farm Environment Controller to a BACnet/IP protocol analyser and a BMS simulator. Trigger a fire alarm condition; confirm alarm receipt at the VFEC within 500 ms. Enable 5-minute polling cycle; confirm energy metrics read via BACnet Read Property service. Verify BACnet Alarm and Event services (clause 13) are enumerated in the device object. | verification-requirements | Verification Requirements |  | Test | 57 |  | IFC-REQ-001 specifies BACnet/IP with 500ms fire alarm latency and 5-minute energy polling. Protocol-level testing against a BMS simulator is the only means to confirm BACnet service compliance and timing. | idempotency:ver-ifc001-bacnet-qc472
VER-REQ-038 | Verify IFC-REQ-002 (REST API crop planning interface): Using an API test client (Postman or equivalent), exercise the VFEC REST endpoints with valid mTLS credentials. Issue crop recipe download, zone scheduling, and log upload requests; measure response time for each (must be ≤5 s under nominal load). Verify 401 rejection when mTLS certificate is absent or expired. | verification-requirements | Verification Requirements |  | Test | 57 |  | IFC-REQ-002 requires mTLS authentication and ≤5s response time. Functional API testing with a valid and invalid certificate is necessary to confirm both authentication and performance acceptance criteria. | idempotency:ver-ifc002-rest-qc472
VER-REQ-039 | Verify IFC-REQ-003 (OpenADR 2.0b and Modbus energy metering): Connect VEN to a certified OpenADR 2.0b VTN test server. Issue a SIMPLE DR event; confirm acknowledgement within 60 seconds. Verify Modbus TCP function codes FC3/FC4 poll energy registers at 15-second interval using a Modbus master test tool; confirm all expected registers respond correctly. | verification-requirements | Verification Requirements |  | Test | 57 |  | IFC-REQ-003 specifies dual protocols (OpenADR VEN and Modbus TCP) with precise timing constraints. Independent protocol testing against a certified OpenADR VTN test instance and a Modbus master is required to validate both interfaces. | idempotency:ver-ifc003-openadr-qc472
VER-REQ-040 | Verify IFC-REQ-004 (MQTT v5 cloud monitoring): Confirm MQTT v5 over TLS 1.3 connection to a cloud broker with all zone sensor, actuator, and alarm topics publishing at 1-minute intervals. Disconnect broker connection; confirm local-only fallback activates within 30 seconds. Restore connection; verify data backfill of buffered telemetry. | verification-requirements | Verification Requirements |  | Test | 57 |  | IFC-REQ-004 requires MQTT v5/TLS 1.3 with 30s fallback and backfill. Disconnection testing is the only way to validate the fallback and reconnection backfill behaviours. | idempotency:ver-ifc004-mqtt-qc472
VER-REQ-041 | Verify IFC-REQ-005 (CO2 bulk supply analogue interface): Inject calibrated 4-20mA signals representing 0%, 20%, 50%, and 100% tank level and 0, 5, 12.5, and 25 bar tank pressure; confirm displayed values at VFEC within ±1% full scale. Set tank level to 20% signal; confirm automatic reorder trigger is generated. Remove 24VDC signal from a zone solenoid output; confirm valve returns to fail-closed state. | verification-requirements | Verification Requirements |  | Test | 57 |  | IFC-REQ-005 specifies 4-20mA analogue inputs and fail-closed solenoid behaviour. Signal injection testing is required to verify analogue scaling and the fail-safe de-energise behaviour. | idempotency:ver-ifc005-co2supply-qc472
VER-REQ-042 | Verify IFC-REQ-015 and IFC-REQ-016 (Safety OPC UA status bus and zone data collection): Configure OPC UA client on Supervisory Control and trigger an interlock trip; confirm interlock state, trip cause code, and last-trip timestamp appear within 1-second poll cycle. Separately, subscribe to Zone Controller Network OPC UA nodes; confirm 1-minute environmental parameter data arrives with UTC timestamp offset ≤1 second. | verification-requirements | Verification Requirements |  | Test | 57 |  | IFC-REQ-015 requires read-only OPC UA status at ≤1s poll; IFC-REQ-016 requires 1-minute zone data with ≤1s timestamp accuracy. Combined OPC UA testing against live controllers confirms both interfaces in one test session. | idempotency:ver-ifc015-016-opcua-qc472
VER-REQ-043 | Verify IFC-REQ-017 (compliance report REST API): Pre-populate TSDB with 90 days of synthetic zone data. Issue an on-demand compliance report request via REST API for a 90-day date range; confirm complete dataset returned within 5 minutes. Issue a partial-range request (7 days); confirm response time proportionally shorter. Verify data integrity by spot-checking 10 random records against TSDB source. | verification-requirements | Verification Requirements |  | Test | 57 |  | IFC-REQ-017 requires report generation within 5 minutes for up to 90-day ranges. Performance testing with maximum-range data confirms the worst-case compliance report response time. | idempotency:ver-ifc017-report-qc472
VER-REQ-044 | Verify SUB-REQ-002 (2oo3 CO2 sensor voting): In a Hardware-in-the-Loop test bench with three CO2 sensor channels wired to the Safety PLC, fail one sensor channel (open circuit); confirm interlock trip is not suppressed and no spurious trip is generated. Fail a second channel while the first remains failed; confirm interlock trip is generated within the required response time. Confirm all three sensors present produces the expected 2oo3 voted output with no spurious trip. Pass criteria: single-channel failure: no spurious trip, 2oo3 voting active; dual-channel failure: interlock trip within 500ms; all channels healthy: no trip, correct CO2 reading. | verification-requirements | Verification Requirements |  | Test | 57 |  | SUB-REQ-002 defines SIL 3 2oo3 voting logic. Hardware channel failure injection on the HIL bench is the only method to verify that the voting architecture correctly distinguishes 1-of-3 sensor failure from actual CO2 exceedance. | idempotency:ver-sub002-2oo3-qc472
VER-REQ-045 | Verify SUB-REQ-003 (Safety PLC IEC 61508 SIL 3 certification): Inspect Safety PLC IEC 61508 third-party certificate confirming SIL 3 capability, 2oo2 dual-core architecture, HFT=1, DC > 99%, and SFF > 99%. Confirm certificate covers the firmware version deployed. Inspect FMEA/FMECA report from the Safety PLC manufacturer. | verification-requirements | Verification Requirements |  | Inspection | 57 |  | SUB-REQ-003 requires third-party SIL 3 certification per IEC 61508. Certification is a hardware supplier deliverable verified by document inspection — functional testing cannot substitute for the PFD calculations underlying SIL 3 classification. | idempotency:ver-sub003-sil3-qc472
VER-REQ-046 | Verify SUB-REQ-004 (Safety PLC scan time and watchdog): Connect an oscilloscope to the Safety PLC scan-complete output pin. Under maximum configured I/O load, measure 100 consecutive scan cycles; confirm all complete within 50 ms. Inhibit the scan-complete signal by injecting a software fault; confirm hardware watchdog asserts safe-state transition within 100 ms. | verification-requirements | Verification Requirements |  | Test | 57 |  | SUB-REQ-004 specifies 50ms scan and 100ms watchdog response. Oscilloscope timing measurement under load is the only direct evidence of compliance; a software fault injection test is required to verify watchdog independence from normal scan completion. | idempotency:ver-sub004-scantime-qc472
VER-REQ-047 | Verify SUB-REQ-006 (interlock trip safe-state response time): In a HIL test environment with live Safety PLC and relay outputs connected to simulated zone loads, assert each interlock trip condition in sequence (CO2 over-threshold, temperature exceedance, manual E-stop). Measure time from condition assertion to output de-energisation for each actuator type (CO2 isolation valve, emergency ventilation, LED circuit breakers, irrigation valves). Confirm safe state is maintained until manual Safety PLC HMI reset. | verification-requirements | Verification Requirements |  | Test | 57 |  | SUB-REQ-006 specifies condition-specific response times for each safe-state output. HIL timing measurements are required for each actuator class; the requirement cannot be verified by inspection because relay propagation delays vary by circuit load. | idempotency:ver-sub006-trip-response-qc472
VER-REQ-048 | Verify SUB-REQ-007 (hardwired trip bus network independence): Disconnect all Modbus, Ethernet, and CAN network cabling from the Safety Interlock Subsystem while a zone is under production recipe control. Assert a CO2 over-threshold condition; confirm the interlock trip actuates correctly via relay chain without any fieldbus communication. Inspect wiring drawings to confirm discrete 24VDC relay circuit topology with no fieldbus dependency. Pass criteria: interlock trip occurs within 500ms of threshold assertion; wiring drawings confirm relay-only topology with zero fieldbus components in trip chain. | verification-requirements | Verification Requirements |  | Test | 43 |  | SUB-REQ-007 requires network-independent trip bus operation. Physical network disconnection testing is the definitive test of independence; inspection of wiring drawings supplements but does not replace live testing. | idempotency:ver-sub007-trip-bus-qc472
VER-REQ-049 | Verify SUB-REQ-008 (LOTO controller energisation prevention): Check out a LOTO key for Zone A; attempt to energise any Zone A equipment via the Supervisory Control HMI and directly via the zone breaker panel; confirm energisation is prevented in both paths. Attempt to energise Zone A equipment again; confirm amber beacon and buzzer activate. Return LOTO key; confirm equipment can be energised normally. | verification-requirements | Verification Requirements |  | Demonstration | 43 |  | SUB-REQ-008 requires personnel safety demonstration to confirm LOTO enforcement. A functional demonstration is the appropriate verification method for a safety-critical personnel protection function. | idempotency:ver-sub008-loto-qc472
VER-REQ-050 | Verify SUB-REQ-013 and SUB-REQ-014 (CO2 Injection Controller setpoint acceptance and software concentration ceiling): Issue Modbus TCP setpoint commands for 400, 1000, and 2000 ppm; confirm acceptance and display at ±1 ppm resolution. Issue out-of-range setpoint (2001 ppm); confirm rejection and alarm. Simulate zone CO2 sensor readings at 2800 ppm; confirm all zone solenoid valves commanded closed. Reduce simulated reading below 2500 ppm; confirm valves remain closed until concentration drops below threshold. | verification-requirements | Verification Requirements |  | Test | 57 |  | SUB-REQ-013 specifies setpoint range 400–2000 ppm at ±1 ppm resolution and rejection of out-of-range commands. SUB-REQ-014 specifies independent 2800/2500 ppm software ceiling. Both must be tested in the same controller test session. | idempotency:ver-sub013-014-co2-setpoint-qc472
VER-REQ-051 | Verify SUB-REQ-015 and SUB-REQ-016 (Zone NDIR CO2 Sensor Array accuracy and autocalibration): Expose sensors to NIST-traceable CO2 calibration gas at 300, 500, 1000, 2000, and 3000 ppm across temperature range 18–35°C and humidity range 40–90% RH; confirm readings within ±100 ppm or ±3% of reading. In a conditioned test chamber, ventilate to ambient CO2 (~420 ppm) for 30+ minutes and trigger autocalibration; confirm calibration log entry with timestamp, pre- and post-calibration readings. | verification-requirements | Verification Requirements |  | Test | 57 |  | SUB-REQ-015 specifies multi-point accuracy across environmental range; SUB-REQ-016 specifies autocalibration with logged output. Multi-point calibration gas injection across the environmental envelope is the only method to verify the ±100 ppm accuracy requirement over operating conditions. | idempotency:ver-sub015-016-ndir-qc472
VER-REQ-052 | Inspect Zone Controller Network installation: verify shielded Cat5e or higher cabling with foil/braid shield markings, IP67-rated junction boxes at each zone entry point, and managed industrial Ethernet switches in Supervisory Control Subsystem enclosure. Verify segment lengths ≤100 m with cable run measurement. Confirm IP67 gasket integrity via visual inspection and pull-test. | verification-requirements | Verification Requirements |  | Inspection |  |  | Physical infrastructure inspection is the appropriate verification method for cable type, IP ratings, and installation compliance. Network segment length can be verified by cable run measurement. IP67 rating is verified by visual inspection of gasket condition and box seal integrity per IEC 60529 assessment criteria. | idempotency:ver-sub-req-095-v1
VER-REQ-053 | Test zone surface material biocompatibility: expose material samples to PAA at 2000 ppm, sodium hypochlorite at 200 ppm, and pH 2.0 and 10.0 solutions for 30 minutes each; inspect for visible degradation, delamination, or surface alteration. After standard sanitisation cycle, swab 10 cm2 samples from 5 random zone surface locations and culture on TSA plates for 48h at 37°C; confirm bioburden below 100 CFU/cm2 in all samples. | verification-requirements | Verification Requirements |  | Test |  |  | Chemical resistance and bioburden testing are the only objective methods to confirm material compatibility with the sanitisation chemistry and food safety cleanliness thresholds. Inspection alone cannot detect subsurface degradation or invisible microbial contamination. Testing against specific concentrations and the 100 CFU/cm2 limit provides quantitative acceptance criteria for material qualification. | idempotency:ver-sub-req-096-v1
VER-REQ-054 | Verify SUB-REQ-009 (Safety PLC network isolation): Audit the network architecture documentation and SCADA/firewall configuration to confirm the Safety PLC connects to the process network exclusively via a certified unidirectional data diode or IEC 62443 SL-2 firewall. Attempt inbound write commands (Modbus FC16 and function block downloads) to Safety PLC I/O addresses from an engineer workstation; confirm all inbound write attempts are blocked. Review firewall access-control lists and data-diode installation records for compliance with the unidirectional communications requirement. Pass criteria: zero successful inbound write transactions; data diode or firewall certificate on file. | verification-requirements | Verification Requirements |  | Inspection |  |  | SIL-3 rated Safety PLC network isolation is a safety-critical cybersecurity control. Any successful inbound write to the Safety PLC could override interlock logic or trip thresholds, defeating the safety function. IEC 61508 SIL-3 requires architectural isolation of the safety system; unidirectional enforcement cannot be verified by analysis alone — active penetration-style inspection and certificate audit are required. Inspection is appropriate here because the isolation is implemented in network hardware (data diode) that can be physically verified, not in software that requires runtime testing. | idempotency:ver-sub009-plc-isolation-477
VER-REQ-055 | Verify SUB-REQ-010 (Voted Logic Engine interlock audit log): In a Hardware-in-the-Loop test environment, trigger 20 synthetic interlock events (CO2 over-threshold, temperature over-threshold, and watchdog failures) in sequence. After each event, query the Safety PLC non-volatile log; confirm each entry contains UTC timestamp (±1s accuracy vs NTP reference), trigger condition identity, all sensor readings at time of trip, and operator reset identity. Continue logging until storage fills above 10,000 events; verify no log entry is overwritten and the oldest entries are preserved. Pass criteria: all 20 triggered events logged with complete fields; capacity ≥10,000 events without loss. | verification-requirements | Verification Requirements |  | Test |  |  | IEC 61508 SIL-3 mandates complete auditability of all safety system state transitions. The audit log is the primary forensic record for incident investigation and proof-test evidence. Testing with 20 synthetic events exercises the log write path, timestamp accuracy, and operator identity capture. Capacity verification prevents a log-overflow vulnerability that could silently lose safety-critical trip records. Inspection of the log format specification alone cannot confirm correct runtime behaviour of the logging mechanism. | idempotency:ver-sub010-audit-log-477
VER-REQ-056 | Verify SUB-REQ-011 (Safety Interlock Subsystem annual proof test): Execute the full SIL-3 proof test procedure: (1) Inject calibrated CO2 at each of the three sensor channels in turn at 5100 ppm; confirm voted-logic trip on 2oo3 pattern; reset and verify return to active interlock monitoring. (2) Actuate each relay output by simulating a trip; confirm the corresponding final element reaches safe state within the specified time bound. (3) Inject a simulated sensor-fail diagnostic on each CO2 channel; verify alarm and continued operation from remaining channels. (4) Record all test results with technician identity, instrument calibration certificates, test date, and outcome in the Safety PLC non-volatile test log. Pass criteria: all exercises pass; test record persisted in Safety PLC log within 60 s of test completion. | verification-requirements | Verification Requirements |  | Demonstration |  |  | IEC 61508 SIL-3 requires periodic proof testing to detect dangerous undetected failures accumulated between online diagnostic cycles. The 12-month proof test interval is consistent with SIL-3 PFD targets and the IEC 61511 proof-test coverage requirements for this type of safety instrumented function. Demonstration (witnessed procedure) is appropriate because proof tests require qualified safety personnel performing the procedure in situ on the commissioned system — it cannot be fully replicated in a factory test or by analysis. Automatic test-log persistence is verified during this procedure. | idempotency:ver-sub011-proof-test-477
VER-REQ-057 | Verify SUB-REQ-045 (Horticultural Lighting emergency shutdown on Safety Interlock trip): In a full-facility integration test with all 8 zone LED Driver Module Arrays energised at recipe setpoints, assert the Safety Interlock hardwired trip bus signal (24V removed). Record de-energisation timestamps per zone using a multi-channel oscilloscope at 1 kHz sample rate. Pass criteria: all LED Driver Modules across all 8 zones de-energised within 5 seconds of trip signal assertion; no zone exceeds the 5-second bound under any combination of fault conditions. Repeat test from three initial lighting states: 100%, 50%, and 10% output level. | verification-requirements | Verification Requirements |  | Test |  |  | Lighting load shedding on safety interlock trip is a SIL-2 safety function — it reduces zone heat load during emergency shutdown when HVAC may also have stopped. The 5-second response time is set by SYS-REQ-009 (thermal protection). Testing across all 8 zones simultaneously is necessary because the hardwired trip bus drives all zones in parallel; a zone-by-zone test would not detect contention or current-limiting failures on the trip bus. Testing at multiple lighting levels verifies the DALI-2 command is acted upon regardless of current output state. | idempotency:ver-sub045-estop-lighting-477
VER-REQ-058 | Verify SUB-REQ-060 (HVAC zone isolation on safety interlock) and SUB-REQ-043 (LCU thermal derating): Part A — Zone isolation: With Zone A HVAC supply and return dampers in energised-open position, assert a zone isolation command from the Safety Interlock Subsystem test port; measure time from command to both dampers fully closed via end-switch feedback; pass criterion: full closure within 2 s. Confirm dampers remain closed when command is maintained; verify damper-open command from Zone Climate Controller is rejected while isolation is held. Part B — Thermal derating: In a test rig with the Lighting Control Unit and Fixture Thermal Monitoring Array, inject simulated heatsink temperature rising at 2 degC/min from 65 degC to 80 degC; confirm 5%/min power reduction begins at 75 degC threshold; verify reduction continues until heatsink falls below 70 degC; pass criteria: derating starts at correct threshold and maintains ≥0.5%/step resolution. | verification-requirements | Verification Requirements |  | Test |  |  | Both requirements protect against thermal runaway pathways. Zone isolation (SUB-REQ-060, SIL-2) prevents heat buildup when the safety system trips other loads; without confirmed damper closure, an isolated zone can overheat within 20 minutes at full lighting. Thermal derating (SUB-REQ-043, SIL-2) prevents LED fixture overtemperature that could lead to fire or early failure; the 75 degC threshold and 5%/min rate are derived from LED manufacturer MTBF curves and IEC 60598-2 luminaire thermal requirements. Both require integration tests because the response paths traverse multiple hardware interfaces that cannot be confirmed by component test alone. | idempotency:ver-sub060-043-hvac-thermal-477
VER-REQ-059 | Verify SUB-REQ-076 (CO2 Enrichment Subsystem independent SIL-2 safety sensor): Inspect the CO2 Enrichment Subsystem installation to confirm a physically separate CO2 sensor, on an independent 24V supply from a dedicated UPS circuit (not shared with the process CO2 sensor supply), with the signal cable routed separately from the process sensor cables. Review the sensor IEC 61508 SIL-2 certificate. Power off the process CO2 sensor supply while the facility is running; confirm the independent safety sensor remains powered and reporting; confirm the process-control CO2 injection controller raises a fault alarm within 5 s. Power off the independent safety sensor supply; confirm a SIL-2 sensor fault alarm is raised within 5 s and CO2 injection is disabled in the affected zone. Pass criteria: independent sensor power and signal path verified by inspection; both fault scenarios produce correct alarm and response within 5 s. | verification-requirements | Verification Requirements |  | Test |  |  | SIL-2 classification of the independent CO2 safety sensor (SUB-REQ-076) requires verified separation from the process-control sensor path — common-cause failure of a shared power rail or signal cable would defeat the independence. Physical inspection alone cannot confirm correct fault response behaviour; power-removal tests verify both the independence of the supply and the correct alarm/disable response of the CO2 injection controller. This is the defence-in-depth layer between a process sensor failure and uncontrolled CO2 accumulation. | idempotency:ver-sub076-co2-safety-sensor-477
VER-REQ-060 | Verify Climate Management Subsystem functional performance (SUB-REQ-054, SUB-REQ-056, SUB-REQ-057, SUB-REQ-058, SUB-REQ-059): In a commissioned grow zone operating at 22 degC / 70% RH setpoints with full crop canopy load: (1) Record zone humidity over 4 hours steady-state; pass criterion: maintained within ±5% RH. (2) Insert a data logger on the Modbus RTU bus and confirm PT100 readings arrive at 1 Hz with ≤2 s end-to-end latency for 1000 consecutive samples. (3) Disconnect one PT100 sensor and confirm Zone Climate Controller switches to the redundant sensor within 10 s and raises a sensor-fault alarm. (4) Monitor Fresh Air Ventilation Controller Modbus TCP messages and confirm fresh air fraction held in 5-30% band during active CO2 enrichment; verify message timing at ≤2 s intervals. (5) Issue a VFD setpoint change command and measure actuator execution confirmation round-trip; pass criterion: ≤500 ms command receipt, ≤1 s status confirmation. | verification-requirements | Verification Requirements |  | Test |  |  | Climate management accuracy (±5% RH, SUB-REQ-054), sensor sampling rate (1 Hz, SUB-REQ-056), sensor failover (SUB-REQ-057), fresh air coordination (5-30%, SUB-REQ-058), and actuator latency (500 ms, SUB-REQ-059) are all performance requirements derived from crop physiology needs. Each must be demonstrated on a commissioned zone under realistic thermal load because the interactions between HVAC actuators, temperature sensor networks, and CO2 enrichment create coupled control loops that cannot be validated by component tests alone. The crop canopy load is specified because it represents the primary thermal disturbance in a vertical farm grow zone. | idempotency:ver-cms-functional-group-477
VER-REQ-061 | Verify Zone Controller Network performance (SUB-REQ-066, SUB-REQ-067, SUB-REQ-068, SUB-REQ-069, SUB-REQ-075): Using a HIL test bench with a Zone Controller Unit, four I/O Expansion Modules, and a Zone Edge Gateway: (1) Measure PID loop execution cycle time over 10,000 iterations using a hardware performance counter; pass criterion: all iterations ≥10 Hz with jitter ≤±5 ms. (2) Issue 10 setpoint updates via OPC-UA; confirm each persisted to non-volatile NOR flash within 5 s via power-cycle recovery test; confirm all setpoints recovered within 10 s of restart. (3) Command all 16 analog inputs on the I/O Expansion Modules to sweep from 4 mA to 20 mA; verify ±0.1% accuracy at 1 Hz; disconnect one 4-20mA loop and confirm open-circuit fault flagged within 60 s. (4) Measure OPC-UA round-trip from sensor acquisition at ZCU to namespace publication at Zone Edge Gateway; pass criterion: ≤500 ms end-to-end. (5) Disconnect OPC-UA network cable from ZCU while zone is active; confirm last-valid setpoint holdover maintained for ≥35 minutes with zone in regulation. | verification-requirements | Verification Requirements |  | Test |  |  | ZCU loop rate (SUB-REQ-066, 10 Hz) determines control bandwidth for all regulated environmental parameters — insufficient loop rate causes steady-state error and overshoot. NOR flash persistence (SUB-REQ-067, 5 s) is the recovery mechanism for power-loss events. I/O sampling accuracy (SUB-REQ-068) underpins all closed-loop control accuracy. Gateway latency (SUB-REQ-069, 500 ms) sets the supervisory loop response time. ZCU holdover (SUB-REQ-075, 35 min) is the primary availability mechanism when supervisory communications fail; testing requires actual power removal to confirm the holdover cache is populated before the outage. | idempotency:ver-zcn-performance-group-477
VER-REQ-062 | Verify REQ-SEVERTICALFARMENV-051 (worker-comfort mode on harvest crew zone entry): In a live test with a zone at full production recipe setpoints (temperature >22 degC, PAR setpoint ≥300 µmol/m2/s, CO2 enrichment active), trigger a zone entry event from the access control reader; confirm within 60 s: temperature setpoint changes to 22 degC, LED white-channel intensity drops to 50% of the previous output, CO2 injection solenoid valve closes and injection control disables for the zone. Attempt to issue a production recipe setpoint restore command while the zone-occupied flag is set; confirm command is rejected. Trigger zone-clear from the access control reader; confirm the system accepts recipe restore commands. Pass criteria: all mode changes within 60 s; zone-occupied interlock prevents production restore; clear signal re-enables recipe commands. | verification-requirements | Verification Requirements |  | Test |  |  | Worker-comfort mode is a safety-critical operational mode protecting harvest crew from CO2 toxicity, photo-biological hazards, and thermal stress. The test uses a live zone because comfort mode parameters interact with the running PID control loops — simulation cannot confirm that CO2 injection shutoff propagates correctly through the closed-loop control or that the zone-occupied flag correctly blocks the supervisory recipe engine. Testing the zone-occupied interlock is mandatory because re-entry to production conditions while crew are present is the primary safety hazard this requirement prevents. | idempotency:ver-worker-comfort-mode-477

## Trace Links
Source Ref | Target Ref | Link Type | Description | Rationale | Created
SUB-REQ-032 | VER-REQ-013 | verifies | Valve fail-safe closure verified by NMS power-loss test | VER-REQ-013 simulates loss of mains power and confirms all zone valves close within 2 seconds, directly testing SUB-REQ-032 normally-closed fail-safe valve specification. | 2026-03-23T00:08:03.313Z
SUB-REQ-030 | VER-REQ-013 | verifies | Stuck-open valve detection verified by NMS integration test | VER-REQ-013 simulates stuck-open irrigation valve and confirms floor drain pump activates within 60 seconds, directly testing SUB-REQ-030 valve fault detection logic. | 2026-03-23T00:08:01.011Z
SUB-REQ-028 | VER-REQ-020 | verifies | Dosing pump safety interlock verified by interlock trip test | VER-REQ-020 simulates safety interlock trip by removing 24VDC relay signal and verifies all zone solenoid valves close, directly testing SUB-REQ-028 hardwired interlock response. | 2026-03-23T00:07:58.777Z
SUB-REQ-026 | VER-REQ-012 | verifies | Dosing pump accuracy verified by pump watchdog test | VER-REQ-012 commands a series of pump injections and confirms volume interlock trip, exercising the SUB-REQ-026 stroke volume accuracy specification under cumulative dosing conditions. | 2026-03-23T00:07:56.549Z
SUB-REQ-025 | VER-REQ-013 | verifies | Sensor fault detection verified by NMS integration test | VER-REQ-013 simulates sensor fault and confirms degraded-mode operation at 50% dosing rate, directly exercising the SUB-REQ-025 fault detection and reporting functions. | 2026-03-23T00:07:53.822Z
SUB-REQ-024 | VER-REQ-013 | verifies | EC/pH sensor accuracy verified by NMS integration test | VER-REQ-013 exercises closed-loop dosing to pH 6.0/EC 2.5 mS/cm setpoints and confirms accuracy within ±0.2 pH and ±0.1 mS/cm, directly testing the SUB-REQ-024 measurement accuracy specification. | 2026-03-23T00:07:51.284Z
SYS-REQ-020 | SUB-REQ-064 | derives | Autonomous operation derives recipe engine continuity | SYS-REQ-020 requires continued autonomous zone regulation from local recipes during cloud outage; SUB-REQ-064 implements this as the Crop Recipe Engine continuing to execute active recipes from local storage. | 2026-03-23T00:07:12.019Z
SYS-REQ-020 | SUB-REQ-073 | derives | Recipe storage system requirement derives crop recipe database | SYS-REQ-020 requires 200 crop recipes in non-volatile storage; SUB-REQ-073 directly implements this as the Crop Recipe Database with 200-recipe capacity and version history. | 2026-03-23T00:07:10.074Z
SYS-REQ-018 | SUB-REQ-052 | derives | System HMI requirement derives supervisory HMI authentication | SYS-REQ-018 specifies supervisory HMI with real-time zone status; SUB-REQ-052 implements the authentication layer for remote HMI sessions, a necessary security function for the system-level HMI capability. | 2026-03-23T00:07:07.919Z
SYS-REQ-017 | SUB-REQ-067 | derives | Failover requirement derives non-volatile recipe persistence | SYS-REQ-017 requires zone regulation restoration within 30s of primary failure; SUB-REQ-067 ensures recipe setpoints persist in NOR flash enabling warm-standby node to resume without retransmission. | 2026-03-23T00:07:05.590Z
SYS-REQ-017 | SUB-REQ-065 | derives | Failover system requirement derives zone controller closed-loop resilience | SYS-REQ-017 requires warm-standby failover within 30s; SUB-REQ-065 specifies the zone controller closed-loop control that the failover node must satisfy after takeover. | 2026-03-23T00:07:03.373Z
SUB-REQ-037 | VER-REQ-013 | derives | SUB-REQ-037 sensor fault fallback verified by Nutrient Management integration test | VER-REQ-013 is the end-to-end Nutrient Management Subsystem test that exercises sensor fault fallback logic specified in SUB-REQ-037. | 2026-03-22T23:04:50.485Z
SUB-REQ-097 | VER-REQ-062 | verifies | Worker-comfort mode SYS requirement verified by live zone integration test | REQ-SEVERTICALFARMENV-052 tests the complete worker-comfort mode entry sequence including CO2 shutoff, lighting reduction, and zone-occupied interlock, satisfying the event-triggered system requirement REQ-SEVERTICALFARMENV-051. | 2026-03-22T22:13:31.135Z
STK-REQ-008 | SUB-REQ-097 | derives | Worker-comfort mode SYS requirement derives from harvest crew safety STK need | STK-REQ-008 requires automatic zone switching to comfort conditions when harvest crew enters; REQ-SEVERTICALFARMENV-051 implements this as a system-level triggered mode requirement with quantified parameters and prevention of automatic return to production. | 2026-03-22T22:13:22.703Z
SUB-REQ-075 | VER-REQ-061 | verifies | SUB-REQ-075 covered by Zone Controller Network HIL performance test | REQ-SEVERTICALFARMENV-050 provides the HIL test bench procedure covering five ZCN performance requirements; SUB-REQ-075 is one of the five test subjects. | 2026-03-22T22:10:56.373Z
SUB-REQ-069 | VER-REQ-061 | verifies | SUB-REQ-069 covered by Zone Controller Network HIL performance test | REQ-SEVERTICALFARMENV-050 provides the HIL test bench procedure covering five ZCN performance requirements; SUB-REQ-069 is one of the five test subjects. | 2026-03-22T22:10:55.731Z
SUB-REQ-068 | VER-REQ-061 | verifies | SUB-REQ-068 covered by Zone Controller Network HIL performance test | REQ-SEVERTICALFARMENV-050 provides the HIL test bench procedure covering five ZCN performance requirements; SUB-REQ-068 is one of the five test subjects. | 2026-03-22T22:10:55.092Z
SUB-REQ-067 | VER-REQ-061 | verifies | SUB-REQ-067 covered by Zone Controller Network HIL performance test | REQ-SEVERTICALFARMENV-050 provides the HIL test bench procedure covering five ZCN performance requirements; SUB-REQ-067 is one of the five test subjects. | 2026-03-22T22:10:54.434Z
SUB-REQ-066 | VER-REQ-061 | verifies | SUB-REQ-066 covered by Zone Controller Network HIL performance test | REQ-SEVERTICALFARMENV-050 provides the HIL test bench procedure covering five ZCN performance requirements; SUB-REQ-066 is one of the five test subjects. | 2026-03-22T22:10:53.784Z
SUB-REQ-059 | VER-REQ-060 | verifies | SUB-REQ-059 covered by Climate Management functional performance integration test | REQ-SEVERTICALFARMENV-049 groups five climate management performance requirements into a single commissioned-zone integration test; SUB-REQ-059 is one of the five sub-tests. | 2026-03-22T22:10:47.023Z
SUB-REQ-058 | VER-REQ-060 | verifies | SUB-REQ-058 covered by Climate Management functional performance integration test | REQ-SEVERTICALFARMENV-049 groups five climate management performance requirements into a single commissioned-zone integration test; SUB-REQ-058 is one of the five sub-tests. | 2026-03-22T22:10:46.408Z
SUB-REQ-057 | VER-REQ-060 | verifies | SUB-REQ-057 covered by Climate Management functional performance integration test | REQ-SEVERTICALFARMENV-049 groups five climate management performance requirements into a single commissioned-zone integration test; SUB-REQ-057 is one of the five sub-tests. | 2026-03-22T22:10:45.756Z
SUB-REQ-056 | VER-REQ-060 | verifies | SUB-REQ-056 covered by Climate Management functional performance integration test | REQ-SEVERTICALFARMENV-049 groups five climate management performance requirements into a single commissioned-zone integration test; SUB-REQ-056 is one of the five sub-tests. | 2026-03-22T22:10:45.129Z
SUB-REQ-054 | VER-REQ-060 | verifies | SUB-REQ-054 covered by Climate Management functional performance integration test | REQ-SEVERTICALFARMENV-049 groups five climate management performance requirements into a single commissioned-zone integration test; SUB-REQ-054 is one of the five sub-tests. | 2026-03-22T22:10:44.469Z
SUB-REQ-076 | VER-REQ-059 | verifies | Independent SIL-2 CO2 safety sensor power separation and fault response verified | SUB-REQ-076 requires independent power path and SIL-2 certification; REQ-048 verifies via supply isolation tests and confirms correct alarm/disable response. | 2026-03-22T22:10:43.803Z
SUB-REQ-043 | VER-REQ-058 | verifies | Lighting Control Unit thermal derating verified by heatsink temperature injection test | SUB-REQ-043 requires 5%/min power derating starting at 75 degC; REQ-047 Part B verifies the threshold and step resolution using injected temperature ramp. | 2026-03-22T22:10:32.930Z
SUB-REQ-060 | VER-REQ-058 | verifies | HVAC zone isolation on safety interlock verified by damper timing test | SUB-REQ-060 requires damper closure within 2 s; REQ-047 Part A provides the commanded-isolation timing test with end-switch confirmation. | 2026-03-22T22:10:32.282Z
SUB-REQ-045 | VER-REQ-057 | verifies | Emergency lighting shutdown on Safety Interlock trip verified across all 8 zones | SUB-REQ-045 requires all LED Driver Modules to de-energise within 5 s of safety trip; REQ-046 tests this across all zones simultaneously with oscilloscope timing measurement. | 2026-03-22T22:10:31.644Z
SUB-REQ-011 | VER-REQ-056 | verifies | Safety Interlock proof test procedure verified by witnessed annual demonstration | SUB-REQ-011 mandates annual proof test; REQ-045 provides the full SIL-3 proof test procedure sequence to be witnessed by a qualified safety engineer. | 2026-03-22T22:10:20.282Z
SUB-REQ-010 | VER-REQ-055 | verifies | Voted Logic Engine audit log verified by HIL test with 20 synthetic interlock events | SUB-REQ-010 requires non-volatile audit log with 10,000 event capacity; REQ-044 tests log write, field completeness, timestamp accuracy, and capacity under overload. | 2026-03-22T22:10:19.596Z
SUB-REQ-009 | VER-REQ-054 | verifies | Safety PLC network isolation verified by inspection and active inbound-write test | SUB-REQ-009 specifies network isolation for SIL-3 Safety PLC; REQ-SEVERTICALFARMENV-043 provides the inspection and active test procedure to confirm unidirectional communications enforcement. | 2026-03-22T22:10:10.987Z
SUB-REQ-096 | VER-REQ-053 | verifies | Verification test procedure for zone biocompatibility requirement | VER-REQ-053 provides the chemical resistance and bioburden test procedure that verifies the material specification in SUB-REQ-096. | 2026-03-22T21:40:23.636Z
SUB-REQ-095 | VER-REQ-052 | verifies | Verification inspection procedure for ZCN physical infrastructure requirement | VER-REQ-052 provides the inspection procedure for the physical cabling and enclosure requirements specified in SUB-REQ-095. | 2026-03-22T21:40:22.984Z
SYS-REQ-016 | SUB-REQ-096 | derives | Zone material biocompatibility derived from sanitisation sequence system requirement | SYS-REQ-016 requires PAA sanitisation sequence; SUB-REQ-096 specifies zone material must withstand PAA at 2000 ppm and meet 100 CFU/cm2 bioburden limit — the material specification enabling the sanitisation sequence to work safely. | 2026-03-22T21:39:41.068Z
SYS-REQ-017 | SUB-REQ-095 | derives | Physical cabling spec derived from zone network failover requirement | SYS-REQ-017 requires 30s zone regulation failover; the physical network cabling specification exists because reliable failover depends on fault-tolerant physical infrastructure in the humid farm environment. | 2026-03-22T21:39:40.421Z
SYS-REQ-017 | SUB-REQ-094 | derives | Zone Controller housing enables system-level failover | Zone Controller physical housing enables system-level failover: physical LRU form factor in accessible enclosures allows swap-out during failover events, making hardware replacement practical without major reinstallation. | 2026-03-22T21:18:06.880Z
SYS-REQ-016 | SUB-REQ-092 | derives | Zone hardware biocompatibility derives from system sanitisation | Zone hardware biocompatibility derives from system sanitisation requirement: hardware installed in zones must use food-safe materials to prevent contamination that would compromise zone sanitisation efficacy. | 2026-03-22T21:17:56.537Z
SYS-REQ-003 | SUB-REQ-091 | derives | CO2 Injection Controller housing derives from system CO2 regulation | CO2 Injection Controller physical housing is required to implement system CO2 regulation: the controller must be installed in a plant-room enclosure to manage pressurised gas and interface with zone solenoid valves. | 2026-03-22T21:17:55.833Z
SYS-REQ-001 | SUB-REQ-090 | derives | Zone Climate Controller housing derives from system temperature control | Zone Climate Controller physical housing is required to implement system temperature control: the controller must be a physically-mountable hardware unit installed in zone enclosures to execute local PID loops. | 2026-03-22T21:17:55.156Z
SYS-REQ-008 | SUB-REQ-081 | derives | ZCC power ride-through derived from HVAC trip controlled response requirement | Zone Climate Controller power supply and ride-through specification derives from SYS-REQ-008 HVAC trip response requirement; the controller must maintain controlled actuator state during supply transients to prevent unintended valve or damper movement at the moment of HVAC trip. | 2026-03-22T20:36:45.840Z
SYS-REQ-016 | SUB-REQ-089 | derives | Zone isolation interlock derived from sanitisation sequence verification requirement | Zone isolation interlock during sanitation directly derives from SYS-REQ-016 sanitisation sequence verification requirement; the interlock is the subsystem-level mechanism that enforces the system-level sanitisation protocol. | 2026-03-22T20:36:33.380Z
SYS-REQ-016 | SUB-REQ-088 | derives | Zone material specification derived from sanitisation and food safety requirement | Food-safe zone material specification derives from SYS-REQ-016 sanitisation sequence requirement; surfaces must be constructed from materials that can withstand repeated chemical sanitisation without leaching contaminants or developing surface porosity. | 2026-03-22T20:36:32.737Z
SYS-REQ-004 | SUB-REQ-087 | derives | CO2 injection controller enclosure derived from CO2 safety interlock requirement | CO2 Injection Controller GRP enclosure and LOTO interface derives from SYS-REQ-004 CO2 safety interlock requirement; the physical design must enable safe manual isolation of CO2 injection under hazardous conditions. | 2026-03-22T20:36:32.117Z
SYS-REQ-008 | SUB-REQ-086 | derives | ZCC enclosure vibration rating derived from HVAC colocation requirement | Zone Climate Controller vibration and enclosure specification derives from SYS-REQ-008 HVAC trip response requirement; the controller must survive vibration from fan motors and compressors while maintaining reliable Modbus communication. | 2026-03-22T20:36:31.491Z
SYS-REQ-011 | SUB-REQ-084 | derives | Network cabling IP67 spec derived from continuous zone telemetry requirement | Network cabling specification derives from SYS-REQ-011 continuous parameter logging requirement; reliable industrial cabling through the growing zone is required to maintain uninterrupted telemetry from zone controllers. | 2026-03-22T20:36:30.828Z
SYS-REQ-003 | SUB-REQ-085 | derives | Enrichment subsystem enclosure derived from CO2 regulation requirement | CO2 Enrichment Subsystem enclosure specification derives from SYS-REQ-003 CO2 regulation requirement; the physical packaging must support reliable solenoid valve operation for precision dosing. | 2026-03-22T20:36:13.701Z
SYS-REQ-001 | SUB-REQ-083 | derives | Zone controller IP54 rating derived from continuous operation in humid growing zone | Zone Controller IP54 DIN-rail packaging derives from SYS-REQ-001 continuous temperature control duty; the controller must survive the high-humidity, misting environment of the growing zone. | 2026-03-22T20:36:12.644Z
SYS-REQ-015 | SUB-REQ-082 | derives | SCS enclosure requirement derived from SIL 2 platform durability constraint | Physical enclosure specification for the Supervisory Control Subsystem derives from SYS-REQ-015 which mandates SIL 2 safety control functions; IP54 industrial packaging is required to ensure environmental durability at that safety integrity level. | 2026-03-22T20:36:11.993Z
SYS-REQ-003 | SUB-REQ-080 | derives | ZCU override enables coordinated zone shutdown | SUB-REQ-080 (ZCU override) derives from SYS-REQ-003: zone regulation tolerance requires coordinated override capability to freeze or shut down zone control loops when sensor faults or emergencies demand it. | 2026-03-22T20:10:47.099Z
SYS-REQ-003 | SUB-REQ-079 | derives | ZCC override enables supervisory environmental regulation | SUB-REQ-079 (ZCC supervisory override) derives from SYS-REQ-003: consistent zone regulation requires the supervisory layer to be able to suspend autonomous zone control during sensor faults or emergencies without triggering uncontrolled excursions. | 2026-03-22T20:10:46.474Z
SUB-REQ-016 | VER-REQ-051 | verifies | NDIR autocalibration log | VER-VER-REQ-051 verifies SUB-REQ-016: NDIR autocalibration log. | 2026-03-22T20:09:12.749Z
SUB-REQ-015 | VER-REQ-051 | verifies | NDIR sensor accuracy across environment | VER-VER-REQ-051 verifies SUB-REQ-015: NDIR sensor accuracy across environment. | 2026-03-22T20:09:12.097Z
SUB-REQ-014 | VER-REQ-050 | verifies | CO2 software concentration ceiling | VER-VER-REQ-050 verifies SUB-REQ-014: CO2 software concentration ceiling. | 2026-03-22T20:09:11.458Z
SUB-REQ-013 | VER-REQ-050 | verifies | CO2 setpoint acceptance and rejection | VER-VER-REQ-050 verifies SUB-REQ-013: CO2 setpoint acceptance and rejection. | 2026-03-22T20:09:10.784Z
SUB-REQ-008 | VER-REQ-049 | verifies | LOTO controller demonstration | VER-VER-REQ-049 verifies SUB-REQ-008: LOTO controller demonstration. | 2026-03-22T20:09:10.109Z
SUB-REQ-007 | VER-REQ-048 | verifies | Hardwired trip bus network independence | VER-VER-REQ-048 verifies SUB-REQ-007: Hardwired trip bus network independence. | 2026-03-22T20:09:09.461Z
SUB-REQ-006 | VER-REQ-047 | verifies | Interlock trip safe-state response time | VER-VER-REQ-047 verifies SUB-REQ-006: Interlock trip safe-state response time. | 2026-03-22T20:09:08.802Z
SUB-REQ-004 | VER-REQ-046 | verifies | Safety PLC scan time and watchdog | VER-VER-REQ-046 verifies SUB-REQ-004: Safety PLC scan time and watchdog. | 2026-03-22T20:09:08.200Z
SUB-REQ-003 | VER-REQ-045 | verifies | Safety PLC SIL 3 certificate inspection | VER-VER-REQ-045 verifies SUB-REQ-003: Safety PLC SIL 3 certificate inspection. | 2026-03-22T20:09:07.509Z
SUB-REQ-002 | VER-REQ-044 | verifies | 2oo3 CO2 sensor voting HIL test | VER-VER-REQ-044 verifies SUB-REQ-002: 2oo3 CO2 sensor voting HIL test. | 2026-03-22T20:09:06.856Z
IFC-REQ-017 | VER-REQ-043 | verifies | Compliance report REST API performance | VER-VER-REQ-043 verifies IFC-REQ-017: Compliance report REST API performance. | 2026-03-22T20:09:06.235Z
IFC-REQ-016 | VER-REQ-042 | verifies | Zone data collection OPC UA subscription | VER-VER-REQ-042 verifies IFC-REQ-016: Zone data collection OPC UA subscription. | 2026-03-22T20:09:05.605Z
IFC-REQ-015 | VER-REQ-042 | verifies | Safety OPC UA status bus timing | VER-VER-REQ-042 verifies IFC-REQ-015: Safety OPC UA status bus timing. | 2026-03-22T20:09:04.945Z
IFC-REQ-005 | VER-REQ-041 | verifies | CO2 supply 4-20mA analogue and fail-closed solenoid | VER-VER-REQ-041 verifies IFC-REQ-005: CO2 supply 4-20mA analogue and fail-closed solenoid. | 2026-03-22T20:09:04.309Z
IFC-REQ-004 | VER-REQ-040 | verifies | MQTT v5 cloud interface with fallback | VER-VER-REQ-040 verifies IFC-REQ-004: MQTT v5 cloud interface with fallback. | 2026-03-22T20:09:03.655Z
IFC-REQ-003 | VER-REQ-039 | verifies | OpenADR VEN and Modbus energy metering | VER-VER-REQ-039 verifies IFC-REQ-003: OpenADR VEN and Modbus energy metering. | 2026-03-22T20:09:02.975Z
IFC-REQ-002 | VER-REQ-038 | verifies | REST API mTLS and response time | VER-VER-REQ-038 verifies IFC-REQ-002: REST API mTLS and response time. | 2026-03-22T20:09:02.306Z
IFC-REQ-001 | VER-REQ-037 | verifies | BACnet/IP interface verified by protocol test | VER-REQ-037 is the BACnet/IP test procedure that directly verifies the 500ms alarm latency and 5-minute polling requirements in IFC-REQ-001. | 2026-03-22T20:08:49.941Z
SYS-REQ-011 | SUB-REQ-077 | derives | Zone OT network security derived from data integrity and cryptographic logging requirement | SYS-REQ-011 requires cryptographic integrity verification of all logged environmental data. Network segmentation and OPC-UA X.509 authentication are necessary conditions for that integrity guarantee — a compromised OT network could inject falsified sensor readings that bypass cryptographic logging, defeating the compliance audit trail. | 2026-03-22T19:41:43.880Z
SYS-REQ-016 | SUB-REQ-078 | derives | Zone material biocompatibility derived from sanitisation sequence and food safety requirement | SYS-REQ-016 requires sanitisation sequence verification before crop recipe activation. The biocompatibility and CIP-compatibility of zone materials is a prerequisite — materials that are not CIP-compatible prevent the peracetic acid sanitisation cycle from being executed reliably, blocking the verification criterion for crop recipe activation. | 2026-03-22T19:41:24.296Z
SYS-REQ-004 | SUB-REQ-076 | derives | Independent SIL-2 CO2 sensor in subsystem derived from SIL-3 safety interlock requirement | SYS-REQ-004 specifies the safety interlock acts on an independent safety-rated CO2 sensor. This SUB requirement decomposes that mandate to the CO2 Enrichment Subsystem, specifying the sensor's certification level (SIL-2), power independence, signal path isolation, and response time budget. | 2026-03-22T19:40:53.938Z
SYS-REQ-017 | SUB-REQ-075 | derives | Zone Controller Unit holdover mode derived from system-level failover requirement | SYS-REQ-017 requires zone regulation functions restored within 30 seconds of primary node failure. The ZCU holdover mode addresses the communication-loss scenario: the ZCU must continue with last-known setpoints for 15 minutes rather than dropping to safe-state immediately, which would interrupt active crop cycles. | 2026-03-22T19:40:32.771Z
SYS-REQ-017 | ARC-REQ-010 | derives | Distributed zone controller architecture derived from failover/warm-standby requirement | SYS-REQ-017 requires 30-second restoration of zone regulation on primary node failure. The distributed ZCU-per-zone architecture enables zone-local control loops to continue during supervisor failover, making the 30-second recovery time achievable without requiring zone controllers to wait for central orchestration. | 2026-03-22T19:39:54.954Z
SYS-REQ-011 | ARC-REQ-011 | derives | Data Acquisition architecture decision derived from environmental logging requirement | SYS-REQ-011 requires 90-day minimum local storage with cryptographic integrity at 1-minute resolution. The TSDB-centred architecture (InfluxDB) with a separate recipe database and automated report generator was chosen because a general-purpose relational database cannot provide the required throughput and time-series compression for this data volume. | 2026-03-22T19:39:45.416Z
SYS-REQ-018 | ARC-REQ-009 | derives | Supervisory Control architecture decision derived from HMI and autonomous recipe requirements | The five-component Supervisory Control decomposition separates server infrastructure from recipe execution to satisfy the browser-accessible HMI requirement alongside the autonomous recipe execution requirement. A monolithic architecture cannot provide both capabilities independently. | 2026-03-22T19:39:44.358Z
SYS-REQ-001 | ARC-REQ-008 | derives | Climate Management architecture decision derived from temperature regulation requirement | The five-component decomposition of Climate Management (sensing, control logic, actuation, ventilation) was driven primarily by the need to satisfy SYS-REQ-001 with a 120-second response time, which requires independent actuation and sensing components that can operate at different timescales. | 2026-03-22T19:39:28.685Z
SYS-REQ-020 | SUB-REQ-064 | derives | Recipe engine continuity during override derived from autonomous operation requirement | SYS-REQ-020 requires 72-hour autonomous zone regulation from stored recipes. The Crop Recipe Engine must continue executing recipes during Plant Management Server override operations; otherwise a routine operator action could suspend environmental control and violate the autonomous operation mandate. | 2026-03-22T19:39:28.008Z
SYS-REQ-001 | SUB-REQ-059 | derives | HVAC actuator interface response time derived from zone temperature regulation response | SYS-REQ-001 requires control loop response within 120 seconds for a 2°C step disturbance. The 500 ms HVAC Actuator Interface response time allocates ≤0.4% of the total response budget to command translation, ensuring the actuator interface is not the bottleneck in the temperature control chain. | 2026-03-22T19:39:07.066Z
SYS-REQ-003 | SUB-REQ-058 | derives | Fresh air ventilation coordination with CO2 derived from CO2 regulation requirement | SYS-REQ-003 requires CO2 within ±50 ppm of setpoint. The Fresh Air Ventilation Controller must coordinate with the CO2 Enrichment Subsystem via Modbus because uncoordinated fresh air intake (high O2, low CO2 outdoor air) directly opposes enrichment, making the ±50 ppm tolerance unachievable without active coordination. | 2026-03-22T19:39:06.286Z
SYS-REQ-014 | SUB-REQ-057 | derives | Sensor fault detection requirement derived from zone isolation and contamination response | SYS-REQ-014 requires zone isolation when contamination is suspected. A Temperature Sensor Network that detects out-of-range or wire-break faults and flags them as sensor drift events is a prerequisite for reliable zone isolation decisions — a faulty temperature reading could mask a real thermal anomaly or trigger incorrect isolation. | 2026-03-22T19:38:53.210Z
SYS-REQ-006 | SUB-REQ-051 | derives | Power envelope for Dosing Pump Array derived from nutrient regulation requirement | SYS-REQ-006 requires dosing pump stroke volume ≤2% tank volume per injection. The 24 VDC supply spec with 30 W and 3 A inrush constraints ensures consistent stepper-driven dosing pump control at the required precision, and enables UPS sizing. | 2026-03-22T19:38:52.570Z
SYS-REQ-006 | SUB-REQ-050 | derives | Power envelope for Irrigation Controller derived from nutrient regulation requirement | SYS-REQ-006 requires precise pH/EC dosing at ≤2% tank volume per stroke. The Irrigation Controller 24 VDC power spec with defined inrush current ensures deterministic stepper actuation and safe panel sizing for this precision dosing. | 2026-03-22T19:38:51.934Z
SYS-REQ-001 | SUB-REQ-056 | derives | Temperature sensor sampling rate derived from temperature regulation response time requirement | SYS-REQ-001 requires control loop response within 120 seconds for a 2°C step disturbance. A 1 Hz minimum sampling rate provides 120 measurement updates within the required response window, giving the PID controller sufficient data density to meet the ±1.0°C setpoint accuracy. | 2026-03-22T19:37:41.598Z
SYS-REQ-020 | IFC-REQ-035 | derives | Recipe Engine to control setpoints interface derives from recipe management requirement | SYS-REQ-020 requires recipe storage and parameter access; IFC-REQ-035 defines the interface through which recipe setpoints flow from the Recipe Engine to zone controllers. | 2026-03-22T19:15:33.957Z
SYS-REQ-001 | IFC-REQ-033 | derives | Zone climate controller HVAC interface supports temperature regulation | SYS-REQ-001 requires ±1.0°C temperature control; IFC-REQ-033 defines the command interface between the Zone Climate Controller and HVAC actuators that delivers this control. | 2026-03-22T19:15:33.300Z
SYS-REQ-020 | IFC-REQ-041 | derives | Supervisory-to-RecipeDB API derives from recipe storage and access requirement | SYS-REQ-020 requires 200 recipe storage and access; IFC-REQ-041 defines the REST interface through which the Supervisory accesses those recipes, making it a direct derivation. | 2026-03-22T19:15:32.660Z
SYS-REQ-017 | SUB-REQ-067 | derives | ZCU setpoint persistence derives from failover recovery requirement | SYS-REQ-017 requires zone regulation within 30s of node failure; SUB-REQ-067 (setpoint flash persistence and retrieval within 10s) is the mechanism that enables this — persisted setpoints allow the ZCU to resume autonomous control immediately after power restoration. | 2026-03-22T19:15:31.996Z
SUB-REQ-074 | VER-REQ-036 | verifies | Compliance report hash and generation time verified by synthetic cycle test | Direct test verification of SUB-REQ-074 acceptance criteria. | 2026-03-22T19:13:28.210Z
IFC-REQ-042 | VER-REQ-035 | verifies | OpenADR-to-Supervisory queue latency verified by end-to-end timing test | Direct test verification of IFC-REQ-042 acceptance criteria. | 2026-03-22T19:13:27.482Z
SUB-REQ-072 | VER-REQ-035 | verifies | OpenADR VEN response timing verified by 10-event test harness | Direct test verification of SUB-REQ-072 acceptance criteria. | 2026-03-22T19:13:26.785Z
SUB-REQ-071 | VER-REQ-034 | verifies | TSDB CSV export performance verified by 100k-record query test | Direct test verification of SUB-REQ-071 acceptance criteria. | 2026-03-22T19:13:26.120Z
SUB-REQ-070 | VER-REQ-034 | verifies | TSDB ingestion fidelity verified by 100k-record injection test | Direct test verification of SUB-REQ-070 acceptance criteria. | 2026-03-22T19:13:25.445Z
IFC-REQ-040 | VER-REQ-034 | verifies | MQTT ingestion interface verified by combined ingest/export test | Direct test verification of IFC-REQ-040 acceptance criteria. | 2026-03-22T19:13:24.803Z
SYS-REQ-020 | SUB-REQ-073 | derives | Recipe database 200-recipe capacity with audit trail derives from system recipe storage requirement | SYS-REQ-020 requires 200 crop recipes and associated parameters; SUB-REQ-073 adds immutable audit trail for GMP compliance, which is the subsystem-level elaboration of that storage requirement. | 2026-03-22T19:13:24.166Z
SYS-REQ-016 | SUB-REQ-074 | derives | Sanitisation verification report derives from sanitisation sequence verification requirement | SYS-REQ-016 requires sanitisation cycle verification including contact time records; SUB-REQ-074 is the specific implementation in the Compliance Report Generator with cryptographic chain of custody. | 2026-03-22T19:13:23.464Z
SYS-REQ-012 | SUB-REQ-072 | derives | OpenADR VEN acknowledgement timing derives from DR event response requirement | SYS-REQ-012 requires response to OpenADR 2.0 events; SUB-REQ-072 specifies the VEN acknowledgement and dispatch timing that fulfils this requirement. | 2026-03-22T19:13:22.716Z
SYS-REQ-011 | SUB-REQ-071 | derives | 30s CSV export derives from system export SLA requirement | SYS-REQ-011 explicitly specifies CSV export within 30 seconds; SUB-REQ-071 is the TSDB-level performance requirement that realises that SLA. | 2026-03-22T19:13:22.052Z
SYS-REQ-011 | SUB-REQ-070 | derives | TSDB 1Hz ingestion and 10-year retention derive from system logging requirement | SYS-REQ-011 specifies 1-second logging with 10-year retention; SUB-REQ-070 is the TSDB implementation of that requirement at subsystem level. | 2026-03-22T19:13:21.434Z
SUB-REQ-065 | VER-REQ-033 | verifies | Verification test for SUB-REQ-065 | Direct integration test verifying the specific parameters of SUB-REQ-065. | 2026-03-22T19:08:59.745Z
IFC-REQ-039 | VER-REQ-032 | verifies | Verification test for IFC-REQ-039 | Direct integration test verifying the specific parameters of IFC-REQ-039. | 2026-03-22T19:08:59.073Z
IFC-REQ-038 | VER-REQ-031 | verifies | Verification test for IFC-REQ-038 | Direct integration test verifying the specific parameters of IFC-REQ-038. | 2026-03-22T19:08:58.430Z
IFC-REQ-037 | VER-REQ-030 | verifies | Verification test for IFC-REQ-037 | Direct integration test verifying the specific parameters of IFC-REQ-037. | 2026-03-22T19:08:57.790Z
SYS-REQ-018 | SUB-REQ-069 | derives | 500ms gateway latency derives from real-time HMI display requirement | SYS-REQ-018 requires real-time HMI; 500ms latency in SUB-REQ-069 is the specific performance budget for the ZCN data path to support that requirement. | 2026-03-22T19:08:34.863Z
SYS-REQ-017 | SUB-REQ-065 | derives | ZCU autonomous operation derives from system failover requirement | SYS-REQ-017 requires zone regulation restored within 30s of primary node failure; the ZCU must maintain setpoints independently during switchover (SUB-REQ-065). | 2026-03-22T19:08:34.214Z
SYS-REQ-011 | SUB-REQ-068 | derives | 1Hz I/O sampling derives from 1-second resolution logging requirement | SYS-REQ-011 requires environmental data logged at ≥1-second resolution; the I/O Expansion Module must sample at ≥1 Hz (SUB-REQ-068) to provide raw data at that resolution before the ZCU processes and forwards it. | 2026-03-22T19:08:02.092Z
SYS-REQ-001 | SUB-REQ-066 | derives | ZCU 10Hz PID rate derives from temperature regulation accuracy requirement | The ±1.0°C tolerance in SYS-REQ-001 sets the closed-loop bandwidth requirement for the ZCU; the 10 Hz control loop rate in SUB-REQ-066 is derived by control system analysis of the zone thermal mass and HVAC actuator response dynamics. | 2026-03-22T19:08:01.443Z
IFC-REQ-036 | VER-REQ-029 | verifies | Hardwired shutdown interface propagation delay test | VER-REQ-029 tests the 20ms propagation latency bound on the hardwired safety interface in IFC-REQ-036. | 2026-03-22T18:43:47.570Z
SUB-REQ-062 | VER-REQ-028 | verifies | Emergency shutdown end-to-end timing test | VER-REQ-028 is the primary acceptance test for SUB-REQ-062, testing the 10s sequence completion time under full-operation conditions. | 2026-03-22T18:43:46.946Z
SYS-REQ-016 | SUB-REQ-063 | derives | Supervisory Control verifies sanitisation sequence completion | SYS-REQ-016 requires automated sanitisation verification; SUB-REQ-063 specifies the sequence steps and compliance record requirement. | 2026-03-22T18:43:00.520Z
SYS-REQ-013 | SUB-REQ-062 | derives | Supervisory Control executes emergency shutdown sequence | SYS-REQ-013 requires the emergency shutdown sequence; SUB-REQ-062 assigns the Emergency Shutdown Sequencer as the responsible actor with 10s total sequence time. | 2026-03-22T18:42:59.825Z
SYS-REQ-012 | SUB-REQ-061 | derives | Supervisory Control implements OpenADR demand response | SYS-REQ-012 mandates OpenADR 2.0 compliance; SUB-REQ-061 specifies the Demand Response Handler implementation with 60s execution window and crop-safety constraints. | 2026-03-22T18:42:59.106Z
IFC-REQ-034 | VER-REQ-027 | verifies | Fresh air/CO2 Modbus TCP integration test | VER-REQ-027 tests the 0.5Hz rate and 200ms latency bound in IFC-REQ-034. | 2026-03-22T18:40:07.230Z
IFC-REQ-032 | VER-REQ-026 | verifies | PT100 bus timing and fault detection test | VER-REQ-026 tests the 1Hz timing and fault detection path specified in IFC-REQ-032. | 2026-03-22T18:40:06.570Z
SUB-REQ-055 | VER-REQ-025 | verifies | Compressor trip 500ms timing test | VER-REQ-025 tests the 500ms response timing of the compressor trip function in SUB-REQ-055. | 2026-03-22T18:40:05.951Z
SUB-REQ-053 | VER-REQ-024 | verifies | Temperature regulation acceptance test | VER-REQ-024 tests the 4-hour steady-state temperature band specified in SUB-REQ-053. | 2026-03-22T18:40:05.316Z
SYS-REQ-014 | SUB-REQ-060 | derives | Climate Management provides damper-based zone isolation | SYS-REQ-014 requires zone airflow isolation on safety command; SUB-REQ-060 specifies the HVAC Actuator Interface damper closure mechanism and 2 s response time. | 2026-03-22T18:37:36.004Z
SYS-REQ-008 | SUB-REQ-055 | derives | Climate Management handles compressor trip lighting reduction | SYS-REQ-008 requires automatic lighting load reduction on HVAC compressor trip; SUB-REQ-055 is the subsystem-level implementation specifying the 500 ms response and economiser fallback. | 2026-03-22T18:37:35.371Z
SYS-REQ-002 | SUB-REQ-054 | derives | Climate Management implements zone humidity control | SYS-REQ-002 requires system-wide RH ±5%; SUB-REQ-054 allocates this to Climate Management with the same quantified band. | 2026-03-22T18:37:34.728Z
SYS-REQ-001 | SUB-REQ-053 | derives | Climate Management implements zone temperature control | SYS-REQ-001 requires system-wide temperature ±1.0 degC; SUB-REQ-053 allocates this to the Climate Management Subsystem as the responsible actor with matching acceptance criterion. | 2026-03-22T18:37:33.998Z
VER-REQ-023 | SUB-REQ-052 | verifies | Authentication and TLS test verifies supervisory control cybersecurity requirement | Authentication and TLS test directly validates the MFA and encryption requirements specified in REQ-SEVERTICALFARMENV-011. | 2026-03-22T18:06:45.962Z
VER-REQ-022 | SYS-REQ-017 | verifies | Failover test verifies VFEC warm-standby redundancy requirement | Failover test directly validates the 30-second restoration window and single-missed-cycle constraint specified in REQ-SEVERTICALFARMENV-008. | 2026-03-22T18:06:45.275Z
VER-REQ-021 | SUB-REQ-049 | verifies | Override response time test verifies zone controller autonomy constraint | Verification procedure directly tests the 500 ms override response window and actuator handover completeness specified in REQ-SEVERTICALFARMENV-007. | 2026-03-22T18:06:44.627Z
STK-REQ-001 | SYS-REQ-017 | derives | Reliability stakeholder need motivates VFEC warm-standby redundancy | STK-REQ-001 requires reliable, continuous crop environment control; REQ-SEVERTICALFARMENV-008 provides the architectural failover mechanism that makes that reliability achievable in the face of processing node failure. | 2026-03-22T18:06:14.173Z
STK-REQ-016 | SYS-REQ-020 | derives | Local recipe storage stakeholder need flows to system specification | STK-REQ-016 requires locally stored crop recipes; REQ-SEVERTICALFARMENV-014 quantifies the derived system requirement (200 recipes, 72h autonomy) to make the stakeholder need verifiable. | 2026-03-22T18:06:13.464Z
STK-REQ-015 | SYS-REQ-019 | derives | EMC stakeholder mandate flows to system compliance requirement | STK-REQ-015 mandates IEC 61000-4 series compliance; REQ-SEVERTICALFARMENV-013 propagates this to the system design specification. | 2026-03-22T18:06:12.811Z
STK-REQ-002 | SYS-REQ-018 | derives | HMI stakeholder need flows down to system-level HMI specification | STK-REQ-002 requires operator HMI for monitoring and adjustment; REQ-SEVERTICALFARMENV-012 derives the quantified system specification (3-interaction acknowledgement, browser-native access) from that stakeholder need. | 2026-03-22T18:06:12.163Z
ARC-REQ-007 | SYS-REQ-005 | derives | Lighting subsystem architecture enables intensity precision compliance | Four-component lighting architecture (lighting control unit, fixture thermal monitoring array, zone controller, and driver circuitry) is required to achieve ±5% LED intensity precision specified in SYS-REQ-005, as thermal variation and driver non-linearity require closed-loop correction. | 2026-03-22T18:04:33.135Z
ARC-REQ-006 | SYS-REQ-006 | derives | Nutrient subsystem architecture enables pH regulatory compliance | Architecture decision to separate dosing control (dosing pump array) from irrigation controller directly implements SYS-REQ-006, which requires pH regulation within ±0.2 — the separation enables independent pH dosing actuation without coupling to bulk irrigation flow. | 2026-03-22T18:04:32.445Z
SYS-REQ-012 | SUB-REQ-048 | derives | LED driver efficiency constrains the energy curtailment depth achievable during demand response | SYS-REQ-012 requires pre-configured curtailment profiles for OpenADR demand response; driver efficiency at 93% minimum means waste heat per zone is bounded, which determines how aggressively the facility can reduce LED power without triggering thermal protection faults during curtailment events | 2026-03-22T17:44:05.411Z
SYS-REQ-005 | SUB-REQ-047 | derives | PAR sensor calibration accuracy is prerequisite for achieving ±5% PAR control accuracy | The ±5% accuracy budget in SYS-REQ-005 must be apportioned between sensor uncertainty, driver accuracy, and PID error; SUB-REQ-047 allocates ±3% to the sensor, requiring ASTM E948 traceability to prevent sensor drift from consuming the entire accuracy budget | 2026-03-22T17:44:04.758Z
SYS-REQ-005 | SUB-REQ-046 | derives | Degraded-mode PAR hold is the resilience mechanism for sustaining PAR control accuracy on sensor failure | SYS-REQ-005 requires PAR accuracy across all operating conditions; SUB-REQ-046 addresses the single-sensor failure mode by specifying a 4-hour hold at last valid PWM, maintaining PAR at the recipe setpoint without closed-loop feedback for a bounded period | 2026-03-22T17:43:54.767Z
SYS-REQ-005 | IFC-REQ-030 | derives | PAR sensor interface enables the closed-loop PPFD feedback required for ±5% accuracy | Without the PAR sensor interface, the LCU cannot close the control loop and cannot achieve SYS-REQ-005 accuracy; the 1Hz sampling rate and loss-of-signal detection are specifically sized for the control bandwidth of the PAR PID loop | 2026-03-22T17:43:54.118Z
SYS-REQ-005 | SUB-REQ-041 | derives | Ramp profile control is the mechanism for transitioning between PAR setpoints | PAR setpoint changes require controlled ramp transitions to avoid photoinhibition; the ramp specification is how the LCU achieves recipe-defined setpoint changes without violating the ±5% accuracy requirement during transitions | 2026-03-22T17:43:53.483Z
SYS-REQ-005 | SUB-REQ-040 | derives | 12-bit spectral channel resolution derives from PAR accuracy requirement | Per-channel dimming resolution is the actuation mechanism for achieving PAR setpoint accuracy; inadequate resolution creates staircase error in the control signal that contributes directly to the PAR accuracy error budget | 2026-03-22T17:43:52.816Z
SYS-REQ-005 | IFC-REQ-013 | derives | PAR setpoint distribution interface derives from system-level PAR accuracy requirement | IFC-REQ-013 defines the interface over which per-zone LED intensity setpoints are distributed from the Zone Controller Network to the HLS — the enabling interface for achieving the PAR accuracy in SYS-REQ-005 | 2026-03-22T17:42:11.978Z
IFC-REQ-031 | VER-REQ-017 | verifies | Fail-safe wiring test verifies IFC-REQ-031 SIL-2 hardwired interface | Three fault-mode test proves normally-closed fail-safe behaviour — the central SIL-2 property of the hardwired interface | 2026-03-22T17:42:11.338Z
IFC-REQ-029 | VER-REQ-016 | verifies | DALI-2 bus timing and addressing test verifies IFC-REQ-029 | Bus analyser test verifies the 22ms response budget and per-channel addressing specified in IFC-REQ-029 | 2026-03-22T17:41:58.201Z
SUB-REQ-042 | VER-REQ-015 | verifies | SIL-2 thermal trip hardware test verifies SUB-REQ-042 | Hardware-loop test of the comparator circuit directly verifies the software-independent trip requirement; 10-shot repeatability provides minimum evidence for SIL-2 reliability claim | 2026-03-22T17:41:56.878Z
SUB-REQ-039 | VER-REQ-014 | verifies | PAR accuracy test verifies SUB-REQ-039 | Multi-point measurement proves the closed-loop accuracy at four setpoints across the full operating range, directly testing the ±5% acceptance criterion | 2026-03-22T17:41:38.419Z
SYS-REQ-013 | SUB-REQ-045 | derives | LED de-energisation step in emergency shutdown sequence | SYS-REQ-013 requires the system to complete emergency shutdown within 10 seconds; SUB-REQ-045 allocates a 5-second sub-budget to the HLS for LED de-energisation as the first step in that sequence | 2026-03-22T17:40:51.329Z
SYS-REQ-008 | SUB-REQ-044 | derives | 50% LED power reduction on HVAC compressor trip | SYS-REQ-008 requires automatic LED power reduction when HVAC trips; SUB-REQ-044 decomposes this into the specific 50% setpoint reduction and 30-second response budget for the LCU | 2026-03-22T17:40:50.700Z
SYS-REQ-009 | SUB-REQ-043 | derives | Software thermal derating at 75 degree C is the graceful pre-trip action | SYS-REQ-009 specifies response to thermal over-temperature; SUB-REQ-043 provides the preventive software derating path that runs before the SIL-2 hardware trip threshold is reached | 2026-03-22T17:40:49.946Z
SYS-REQ-009 | SUB-REQ-042 | derives | 85 degree C fixture thermal trip allocated to HLS thermal monitoring | SYS-REQ-009 specifies de-energisation at 85 degree C fixture temperature; SUB-REQ-042 implements this via the hardware-independent comparator path in the Fixture Thermal Monitoring Array | 2026-03-22T17:40:49.281Z
SYS-REQ-005 | SUB-REQ-039 | derives | PAR control accuracy requirement allocates to HLS | SYS-REQ-005 sets the system-level ±5% PAR accuracy; SUB-REQ-039 decomposes this into a closed-loop PPFD control requirement for the Horticultural Lighting Subsystem | 2026-03-22T17:40:48.593Z
VER-REQ-013 | SYS-REQ-006 | verifies | NMS end-to-end test verifies system-level pH/EC control and flood prevention | VER-REQ-013 tests closed-loop pH/EC setpoint achievement (verifying SYS-REQ-006), stuck-valve flood detection (verifying SYS-REQ-010), degraded-mode operation (verifying SYS-REQ-007 fallback), and power-loss fail-safe (verifying SYS-REQ-013 safe state). The end-to-end NMS test is the primary system-level evidence for SYS-REQ-006 compliance. | 2026-03-22T17:15:02.463Z
SYS-REQ-006 | IFC-REQ-028 | derives | Pump suction interface defines physical connection for nutrient solution circulation | SYS-REQ-006 requires pH/EC regulation through dosing and circulation. IFC-REQ-028 defines the physical connection between the Recirculation Pump System and the Nutrient Reservoir — the interface at which solution enters the pump for distribution. This interface requires a hardwired dry-run protection switch that operates independently of software, a design constraint that exists to protect the food safety requirement embedded in SYS-REQ-006. | 2026-03-22T17:15:01.755Z
SYS-REQ-006 | IFC-REQ-026 | derives | IC to DPA Modbus TCP interface enables closed-loop dosing command chain | SYS-REQ-006 requires closed-loop pH/EC control. IFC-REQ-026 specifies the command interface between the Irrigation Controller and Dosing Pump Array through which pump enable commands and injection confirmations flow. Without this interface definition, the control loop from SYS-REQ-006 has no specified command path between the controller and the actuator. | 2026-03-22T17:15:01.093Z
SYS-REQ-007 | SUB-REQ-037 | derives | Degraded-mode dosing rate limit balances crop continuity against sensor-drift overdose risk | SYS-REQ-007 flags sensor drift as a potential overdose hazard. SUB-REQ-037 specifies a 50% rate-limited open-loop fallback that acknowledges the sensor-fault risk from SYS-REQ-007 while avoiding complete cessation of dosing (which would harm the crop). The 50% rate reduction derives from the safety margin required to ensure that even in sensor-fault open-loop mode, cumulative injection stays below the 5% watchdog threshold for the typical fault detection and response window. | 2026-03-22T17:14:48.850Z
SYS-REQ-006 | SUB-REQ-036 | derives | Reservoir low-level alarm supports operator intervention before dosing loss | SYS-REQ-006 requires continuous pH/EC regulation. SUB-REQ-036 ensures operators are warned before the working solution volume falls to a level that would cause pump dry-run and dosing cessation. The alarm is directly driven by the need to maintain continuous nutrient delivery required by SYS-REQ-006. | 2026-03-22T17:14:48.211Z
SYS-REQ-006 | SUB-REQ-035 | derives | Dry-run protection preserves pump integrity for sustained nutrient delivery | SYS-REQ-006 requires sustained nutrient solution management. SUB-REQ-035 protects the recirculation pump from seal failure caused by dry running — a failure mode that would release pump materials into the food crop nutrient solution and cause an uncontrolled shutdown. Pump integrity is therefore a prerequisite for reliable compliance with SYS-REQ-006. | 2026-03-22T17:14:47.514Z
SYS-REQ-006 | SUB-REQ-034 | derives | Pump duty/standby availability supports continuous pH/EC dosing and delivery | SYS-REQ-006 requires pH and EC to be maintained within tolerance, which is only possible while nutrient solution is circulating. SUB-REQ-034 ensures pump failure does not cause a prolonged interruption to that circulation. Without automatic standby changeover, a single pump failure would halt dosing feedback and nutrient delivery, making SYS-REQ-006 compliance intermittent. | 2026-03-22T17:14:34.008Z
SYS-REQ-010 | SUB-REQ-033 | derives | Valve position feedback is required for the 30-second stuck-valve detection | SYS-REQ-010 requires stuck-valve detection within 30 seconds. SUB-REQ-033 provides the detection mechanism: without position feedback confirming that a valve is stuck open despite a close command, the Irrigation Controller cannot distinguish between normal valve settling delay and a genuine stuck-open fault. Position feedback is therefore a direct technical prerequisite of the stuck-valve detection requirement. | 2026-03-22T17:14:33.295Z
SYS-REQ-010 | SUB-REQ-032 | derives | Normally-closed fail-safe valve closure supports stuck-valve flood prevention | SYS-REQ-010 requires stuck-valve detection and zone isolation within 30 seconds. SUB-REQ-032 specifies the valve array must be normally-closed (fail-safe on power loss), which is the mechanical prerequisite: if valves were normally-open, loss of power during detection/isolation would cause flooding rather than prevent it. The fail-safe property is therefore directly required by SYS-REQ-010. | 2026-03-22T17:14:32.626Z
SYS-REQ-006 | SUB-REQ-029 | derives | Irrigation scheduling enables controlled nutrient solution delivery for pH/EC control | SYS-REQ-006 requires pH and EC to be maintained within tight tolerances. The Irrigation Controller scheduling requirement (SUB-REQ-029) exists to ensure nutrient solution reaches every zone on a controlled cycle and that simultaneous multi-zone demand does not collapse distribution pressure — both preconditions for reliable closed-loop pH/EC control. | 2026-03-22T17:14:17.075Z
SYS-REQ-007 | SUB-REQ-028 | derives | Dosing pump safe state derives from overdose protection trip response | SYS-REQ-007 requires dosing suspension when the overdose threshold is crossed. SUB-REQ-028 specifies the mechanical safe state at the pump level — inhibiting all pump outputs on interlock trip — which is the component-level implementation of the system-level dosing suspension requirement. | 2026-03-22T17:14:16.450Z
SYS-REQ-007 | SUB-REQ-025 | derives | Sensor fault detection enables dosing suspension decision in overdose protection | SYS-REQ-007 treats continued dosing without pH equilibration as sensor drift and requires suspension. SUB-REQ-025 is the prerequisite mechanism: the EC/pH Sensor Array must report its own fault state so the Irrigation Controller can detect the sensor-drift condition. Without fault reporting, SYS-REQ-007 cannot be implemented. | 2026-03-22T17:14:15.801Z
SUB-REQ-027 | VER-REQ-012 | verifies | SIL-2 functional test for Dosing Pump Array hardwired watchdog | VER-REQ-012 verifies the 200ms signal propagation time and the latched-trip behaviour of SUB-REQ-027. The test uses below-threshold and above-threshold injection scenarios to validate both the absence of spurious trips and the correct threshold detection — the minimum test coverage for a SIL-2 function per IEC 61508. | 2026-03-22T17:13:22.377Z
IFC-REQ-027 | VER-REQ-011 | verifies | Integration test for Irrigation Controller to Zone Irrigation Valve Array interface | VER-REQ-011 verifies the 24VAC actuation timing (2s open/close confirmation), position feedback path, and stuck-valve fault detection (30s) specified in IFC-REQ-027. The stuck-valve scenario directly tests the primary safety-relevant path in this interface. | 2026-03-22T17:13:13.447Z
IFC-REQ-025 | VER-REQ-010 | verifies | Integration test for EC/pH Sensor Array to Irrigation Controller Modbus interface | VER-REQ-010 verifies the accuracy (±0.1 mS/cm EC, ±0.05 pH), protocol (Modbus RTU RS-485, 9600 baud), and fault detection path (5-second fault flag propagation) specified in IFC-REQ-025. These three attributes are the complete set of verifiable claims in IFC-REQ-025. | 2026-03-22T17:13:12.775Z
SYS-REQ-016 | SUB-REQ-031 | derives | Sanitisation sequence execution derives from zone changeover compliance | SYS-REQ-016 requires sanitisation verification before crop recipe activation. SUB-REQ-031 cascades the specific chemical parameters (≥80 ppm peracetic acid, ≥20 min contact, EC/pH confirmation) to the Irrigation Controller as the component responsible for commanding the flush/drain cycle. The parameters come from food-safety CIP standards referenced in SYS-REQ-016's compliance rationale. | 2026-03-22T17:13:12.146Z
SYS-REQ-010 | SUB-REQ-030 | derives | Irrigation Controller stuck-valve detection derives from flood prevention system req | SYS-REQ-010 mandates stuck-valve detection within 30 seconds and drain pump activation within 60 seconds. SUB-REQ-030 allocates this detection function to the Irrigation Controller because it is the component with both valve command authority and flow meter input — the only component that can compare commanded state against actual flow. Without this allocation, no component would own the detection logic. | 2026-03-22T17:13:11.499Z
SYS-REQ-007 | SUB-REQ-027 | derives | Hardwired dosing-excess watchdog derives from SIL-2 overdose protection | SYS-REQ-007 requires suspension of dosing when cumulative injection exceeds 5% of tank volume in 10 minutes. SUB-REQ-027 implements this as a hardwired SIL-2 function in the Dosing Pump Array, with the specific 200ms propagation time derived from SIL-2 diagnostic requirements. This is a direct functional cascade. | 2026-03-22T17:12:55.285Z
SYS-REQ-006 | SUB-REQ-026 | derives | Pump stroke volume limit derives from overshoot prevention requirement | SYS-REQ-006 explicitly constrains dosing pump stroke volume to 2% of tank volume per injection. SUB-REQ-026 cascades this constraint directly to the Dosing Pump Array component, adding the ±1% accuracy requirement to ensure the 2% limit is not exceeded by calibration error. The component requirement would not exist without this specific system constraint. | 2026-03-22T17:12:54.657Z
SYS-REQ-006 | SUB-REQ-024 | derives | EC/pH sensor accuracy derives from nutrient control setpoint tolerances | SYS-REQ-006 specifies ±0.1 mS/cm EC and ±0.2 pH system-level accuracy. SUB-REQ-024 exists specifically because the EC/pH Sensor Array must achieve the sensor-level accuracy that makes these system tolerances achievable; the component requirement directly cascades from the system tolerance allocation. | 2026-03-22T17:12:53.737Z
SYS-REQ-003 | SUB-REQ-023 | derives | UPS requirement to maintain CO2 regulation during power interruptions | CO2 injection must continue during mains power interruptions to avoid crop stress from sudden CO2 removal; UPS ensures the CO2 Injection Controller remains operational for the duration needed for orderly zone shutdown | 2026-03-22T16:42:26.720Z
SYS-REQ-003 | SUB-REQ-021 | derives | Degraded mode for sensor fault to maintain regulation in other zones | SYS-REQ-003 applies to all zones; when one zone sensor fails, closing that zone's valve preserves measurement validity for remaining zones while preventing uncontrolled enrichment in the faulted zone | 2026-03-22T16:42:26.081Z
SYS-REQ-003 | SUB-REQ-020 | derives | Manifold material requirement ensures CO2 service integrity | Manifold integrity is a precondition for reliable CO2 delivery; material and pressure-test requirements ensure the manifold does not contribute leakage or failure modes that would compromise SYS-REQ-003 regulation | 2026-03-22T16:42:25.413Z
SYS-REQ-003 | SUB-REQ-019 | derives | Manifold pressure regulation enables consistent zone injection | Consistent CO2 injection across all zones (required for ±50 ppm regulation) depends on stable manifold pressure; SUB-REQ-019 ensures the pressure variation that drives injection flow is controlled | 2026-03-22T16:42:24.763Z
SYS-REQ-003 | SUB-REQ-018 | derives | Valve leakage requirement to prevent uncontrolled CO2 enrichment | Valve seat leakage during closed state would create uncontrolled CO2 enrichment; this requirement establishes the leakage bound that keeps leakage-induced concentration rise negligible and maintains SYS-REQ-003 regulation integrity | 2026-03-22T16:42:24.132Z
SYS-REQ-003 | IFC-REQ-024 | derives | CO2 regulation requires manifold pressure monitoring interface | CO2 concentration regulation per SYS-REQ-003 depends on reliable CO2 supply; manifold pressure monitoring is the means by which supply exhaustion is detected before it disrupts injection | 2026-03-22T16:42:23.485Z
SYS-REQ-004 | VER-REQ-009 | verifies | System-level CO2 over-concentration trip verification | End-to-end test measures the full trip response time from sensor reading through hardwired relay to valve closure, verifying the 2-second system requirement | 2026-03-22T16:40:49.837Z
SYS-REQ-003 | VER-REQ-009 | verifies | System-level CO2 regulation verification | End-to-end test provides system-level evidence that ±50 ppm regulation is achievable end-to-end including supervisory communication, controller, sensors, and valves | 2026-03-22T16:40:49.201Z
IFC-REQ-023 | VER-REQ-008 | verifies | Valve command/feedback interface test | Tests normal valve operation timing and fault detection capability | 2026-03-22T16:40:48.624Z
IFC-REQ-022 | VER-REQ-007 | verifies | Interface test for NDIR sensor 4-20mA analogue signal | Tests signal calibration and open-circuit fault detection for the process sensor interface | 2026-03-22T16:40:48.020Z
SUB-REQ-022 | VER-REQ-020 | verifies | SIL-3 safe state functional test for CO2 subsystem | Verifies hardwired trip mechanism, software lockout, and operator reset behaviour required by IEC 61508-2 for SIL-3 function | 2026-03-22T16:40:22.736Z
SUB-REQ-017 | VER-REQ-019 | verifies | Valve closure time test across temperature range | Tests valve closure time at boundary temperature conditions against 500ms specification allocated from SIL-3 trip budget | 2026-03-22T16:40:22.077Z
SUB-REQ-012 | VER-REQ-018 | verifies | PID performance test for CO2 injection controller | Test verifies steady-state and transient accuracy of PID control loop against ±50 ppm specification | 2026-03-22T16:40:21.268Z
SYS-REQ-015 | SUB-REQ-022 | derives | SIL-3 allocation for CO2 interlock cascades to subsystem safe state requirement | SYS-REQ-015 establishes SIL-3 for the CO2 interlock function; SUB-REQ-022 is the implementation of that SIL-3 function at the CO2 Enrichment Subsystem boundary | 2026-03-22T16:38:31.200Z
SYS-REQ-004 | SUB-REQ-022 | derives | CO2 over-concentration interlock drives CO2 subsystem safe state | SYS-REQ-004 defines the system-level safety response; SUB-REQ-022 is the CO2 Enrichment Subsystem-specific realisation of that response, defining the hardwired trip mechanism and the operator-reset lockout | 2026-03-22T16:38:30.565Z
SYS-REQ-004 | SUB-REQ-017 | derives | 5000 ppm trip response drives valve closure time budget | SYS-REQ-004 requires full trip response within 2s; SUB-REQ-017 allocates 500ms of that budget to the valve stroke time, derived from partitioning the 2s trip budget across PLC scan, relay actuation, and mechanical valve closure | 2026-03-22T16:38:29.890Z
SYS-REQ-003 | SUB-REQ-016 | derives | CO2 concentration regulation derives to CO2 Enrichment Subsystem component | SYS-REQ-003 requires ±50 ppm regulation; SUB-REQ-016 implements the specific component behaviour (PID loop, setpoint acceptance, NDIR sensing) that collectively fulfils this system-level requirement | 2026-03-22T16:38:17.872Z
SYS-REQ-003 | SUB-REQ-015 | derives | CO2 concentration regulation derives to CO2 Enrichment Subsystem component | SYS-REQ-003 requires ±50 ppm regulation; SUB-REQ-015 implements the specific component behaviour (PID loop, setpoint acceptance, NDIR sensing) that collectively fulfils this system-level requirement | 2026-03-22T16:38:17.242Z
SYS-REQ-003 | SUB-REQ-014 | derives | CO2 concentration regulation derives to CO2 Enrichment Subsystem component | SYS-REQ-003 requires ±50 ppm regulation; SUB-REQ-014 implements the specific component behaviour (PID loop, setpoint acceptance, NDIR sensing) that collectively fulfils this system-level requirement | 2026-03-22T16:38:16.621Z
SYS-REQ-003 | SUB-REQ-013 | derives | CO2 concentration regulation derives to CO2 Enrichment Subsystem component | SYS-REQ-003 requires ±50 ppm regulation; SUB-REQ-013 implements the specific component behaviour (PID loop, setpoint acceptance, NDIR sensing) that collectively fulfils this system-level requirement | 2026-03-22T16:38:15.987Z
SYS-REQ-003 | SUB-REQ-012 | derives | CO2 concentration regulation derives to CO2 Enrichment Subsystem component | SYS-REQ-003 requires ±50 ppm regulation; SUB-REQ-012 implements the specific component behaviour (PID loop, setpoint acceptance, NDIR sensing) that collectively fulfils this system-level requirement | 2026-03-22T16:38:15.313Z
IFC-REQ-013 | VER-REQ-006 | verifies | Process network interface latency/accuracy verification | VER-REQ-006 exercises all process network interfaces under simultaneous load, directly verifying the latency and accuracy specifications of IFC-REQ-013. | 2026-03-22T16:12:47.044Z
IFC-REQ-012 | VER-REQ-006 | verifies | Process network interface latency/accuracy verification | VER-REQ-006 exercises all process network interfaces under simultaneous load, directly verifying the latency and accuracy specifications of IFC-REQ-012. | 2026-03-22T16:12:46.432Z
IFC-REQ-011 | VER-REQ-006 | verifies | Process network interface latency/accuracy verification | VER-REQ-006 exercises all process network interfaces under simultaneous load, directly verifying the latency and accuracy specifications of IFC-REQ-011. | 2026-03-22T16:12:45.782Z
IFC-REQ-010 | VER-REQ-006 | verifies | Process network interface latency/accuracy verification | VER-REQ-006 exercises all process network interfaces under simultaneous load, directly verifying the latency and accuracy specifications of IFC-REQ-010. | 2026-03-22T16:12:45.132Z
IFC-REQ-009 | VER-REQ-006 | verifies | Process network interface latency/accuracy verification | VER-REQ-006 exercises all process network interfaces under simultaneous load, directly verifying the latency and accuracy specifications of IFC-REQ-009. | 2026-03-22T16:12:44.503Z
IFC-REQ-019 | VER-REQ-005 | verifies | Hardwired dosing-excess signal latency verification | VER-REQ-005 includes injection of dosing-excess fault signal to verify the 200ms propagation specification of IFC-REQ-019. | 2026-03-22T16:12:43.793Z
IFC-REQ-018 | VER-REQ-005 | verifies | Hardwired thermal trip signal latency verification | VER-REQ-005 includes injection of zone temperature over-threshold signal to verify the 100ms propagation specification of IFC-REQ-018. | 2026-03-22T16:12:43.109Z
IFC-REQ-014 | VER-REQ-005 | verifies | Hardwired CO2 trip signal latency verification | VER-REQ-005 includes combined hardwired input injection that directly tests the 500ms propagation requirement of IFC-REQ-014 using a calibrated signal logger. | 2026-03-22T16:12:42.456Z
SYS-REQ-001 | IFC-REQ-021 | derives | Zone fault event interface supports real-time zone status monitoring | SYS-REQ-001 requires real-time zone monitoring and control. IFC-REQ-021 defines the OPC UA event publication from Zone Controllers to Supervisory Control for fault events, enabling the supervisory layer to detect zone deviations within the 5-second HMI update window required by STK-REQ-001. | 2026-03-22T16:11:56.008Z
SYS-REQ-003 | IFC-REQ-020 | derives | CO2 setpoint distribution interface derived from CO2 regulation requirement | SYS-REQ-003 requires CO2 regulation within ±50 ppm of crop recipe setpoints. IFC-REQ-020 defines the Modbus TCP/IP interface over which the Supervisory Control distributes CO2 setpoints from the crop recipe to the CO2 Enrichment Subsystem. | 2026-03-22T16:11:55.389Z
SYS-REQ-007 | IFC-REQ-019 | derives | Hardwired dosing-excess signal derives from pH safety trip requirement | SYS-REQ-007 requires the dosing-excess condition to trigger a safety trip within 5 seconds. IFC-REQ-019 defines the hardwired 24VDC contact closure from Nutrient Management to Safety PLC that delivers this signal within 200ms, independent of the Modbus process network. | 2026-03-22T16:11:54.776Z
SYS-REQ-009 | IFC-REQ-018 | derives | Hardwired thermal trip signal derives from zone temperature exceedance requirement | SYS-REQ-009 requires thermal trip within 10 seconds when zone exceeds 38°C. IFC-REQ-018 defines the hardwired 24VDC contact closure from Climate Management to Safety PLC that delivers the thermal over-temperature signal within 100ms, satisfying the independence from process network required by SYS-REQ-015. | 2026-03-22T16:11:54.117Z
SYS-REQ-011 | IFC-REQ-017 | derives | Compliance report generation interface supports SYS logging requirement | SYS-REQ-011 requires compliance reporting capability. IFC-REQ-017 defines the REST API interface between Supervisory Control and Data Acquisition for on-demand compliance report generation, isolating the compliance store from operational control traffic. | 2026-03-22T16:11:53.420Z
SYS-REQ-011 | IFC-REQ-016 | derives | Zone data collection interface implements compliance logging requirement | SYS-REQ-011 requires logging all environmental parameters at 1-minute resolution for 90 days. IFC-REQ-016 defines the OPC UA subscription interface from Data Acquisition to Zone Controllers that collects this data, with UTC ±1 second timestamping required for compliance audit correlation. | 2026-03-22T16:11:39.183Z
SYS-REQ-015 | IFC-REQ-015 | derives | Unidirectional safety status interface enforces SIL 3 independence | SYS-REQ-015 mandates safety functions operate independently from process control. IFC-REQ-015 defines the unidirectional OPC UA status bus from Safety Interlock to Supervisory Control that enforces this independence: supervisory software can read safety state but cannot write to it. | 2026-03-22T16:11:38.512Z
SYS-REQ-004 | IFC-REQ-014 | derives | Hardwired CO2 shutoff interface implements software-independent interlock | SYS-REQ-004 requires CO2 interlock independent of software with 10-second shutoff. IFC-REQ-014 defines the hardwired de-energize-to-trip interface that implements this independence, with 500ms propagation leaving 9.5 seconds for actuator stroke. | 2026-03-22T16:11:37.876Z
SYS-REQ-005 | IFC-REQ-013 | derives | LED control interface derived from lighting accuracy and thermal protection requirements | SYS-REQ-005 requires LED intensity within ±5% of recipe setpoints. IFC-REQ-013 defines the DALI-2/DMX512 interface for LED control with ±1% dimming accuracy and surface temperature telemetry at 0.2Hz needed to satisfy SYS-REQ-009 thermal protection. | 2026-03-22T16:11:37.221Z
SYS-REQ-006 | IFC-REQ-012 | derives | Nutrient dosing interface derived from pH regulation requirement | SYS-REQ-006 requires pH regulation within ±0.2. IFC-REQ-012 defines the Nutrient Management to Zone Controller Network interface that provides the per-zone pH feedback and dosing commands needed for closed-loop pH control. | 2026-03-22T16:11:23.809Z
SYS-REQ-008 | IFC-REQ-011 | derives | HVAC actuator command interface enables degraded-mode fault detection | SYS-REQ-008 requires degraded-mode HVAC operation with 1-second fault detection. IFC-REQ-011 defines the Climate Management to Zone Controller Network interface with 1-second acknowledgement, which is the mechanism by which actuator faults are detected and degraded-mode responses triggered. | 2026-03-22T16:11:23.179Z
SYS-REQ-003 | IFC-REQ-010 | derives | CO2 feedback interface derived from 50ppm regulation requirement | SYS-REQ-003 requires CO2 regulation within ±50 ppm. IFC-REQ-010 defines the CO2 Enrichment Subsystem to Zone Controller Network feedback interface at 1Hz needed for the closed-loop CO2 control that achieves this accuracy. | 2026-03-22T16:11:22.508Z
SYS-REQ-001 | IFC-REQ-009 | derives | Zone setpoint distribution interface derived from temperature control requirement | SYS-REQ-001 requires zone temperature control within ±1°C. IFC-REQ-009 defines the Supervisory Control to Zone Controller Network interface over which setpoints are transmitted. The 500ms latency bound is derived from the need to distribute recipe changes within the 60-second window required by STK-REQ-002. | 2026-03-22T16:11:21.847Z
SYS-REQ-011 | ARC-REQ-005 | derives | Data acquisition separation enables independent compliance data management | SYS-REQ-011 requires 90-day data retention and compliance reporting. ARC-REQ-005 records the decision to separate Data Acquisition from supervisory control, enabling the compliance data store to be sized and retained independently. | 2026-03-22T16:11:08.445Z
SYS-REQ-012 | ARC-REQ-004 | derives | Energy optimisation co-location enables demand-response capability | SYS-REQ-012 requires demand-response and energy optimisation. ARC-REQ-004 records the decision to co-locate energy optimisation with supervisory control, enabling OpenADR demand-response to access both real-time setpoints and historical energy data. | 2026-03-22T16:11:07.786Z
SYS-REQ-004 | ARC-REQ-003 | derives | CO2 subsystem separation maintains SIL 3 boundary | SYS-REQ-004 requires CO2 interlock with SIL 3 independence. ARC-REQ-003 records the decision to separate CO2 Enrichment from Climate Management to maintain the SIL 3 boundary required by SYS-REQ-004. | 2026-03-22T16:11:07.113Z
SYS-REQ-008 | ARC-REQ-002 | derives | Distributed zone architecture enables per-zone degraded-mode | SYS-REQ-008 requires degraded-mode operation when a zone HVAC compressor trips. ARC-REQ-002 records the distributed zone controller architecture decision that enables per-zone independent degraded-mode operation without a central failure point. | 2026-03-22T16:11:06.458Z
SYS-REQ-015 | ARC-REQ-001 | derives | Safety interlock architecture implements software independence | SYS-REQ-015 mandates safety-critical functions operate independently of process control software. ARC-REQ-001 records the architecture decision to implement the Safety Interlock Subsystem as hardware-independent relay, which is the specific design choice enabling compliance with SYS-REQ-015. | 2026-03-22T16:11:05.843Z
STK-REQ-004 | SYS-REQ-014 | derives | Zone isolation for maintenance directly implements STK-REQ-004 | STK-REQ-004 requires enabling zone maintenance without disrupting active crop cycles. SYS-REQ-014 defines the zone airflow and nutrient isolation capability that implements this maintenance isolation — the system must be able to isolate a single zone's HVAC dampers and nutrient supply while adjacent zones continue operating. | 2026-03-22T16:10:05.214Z
STK-REQ-001 | SYS-REQ-010 | derives | Irrigation fault detection is part of zone environmental monitoring | STK-REQ-001 requires zone-specific environmental status monitoring including nutrient system health. SYS-REQ-010 specifies irrigation valve fault detection, which is a component of the environmental monitoring capability the Grower Technician requires for daily crop management. | 2026-03-22T16:10:04.551Z
STK-REQ-001 | SYS-REQ-002 | derives | Zone humidity control derives from grower technician operational needs | STK-REQ-001 requires zone-specific environmental dashboards and control. SYS-REQ-002 specifies the humidity control performance (±5% RH) that implements the zone-specific climate control capability the Grower Technician stakeholder requires to maintain optimal crop growing conditions. | 2026-03-22T16:10:03.891Z
SYS-REQ-013 | SUB-REQ-008 | derives | LOTO controller implements energy isolation component of emergency shutdown | SYS-REQ-013 requires emergency shutdown with zone isolation including locking out energy sources. SUB-REQ-008 specifies the Lockout Tagout Controller behaviour that prevents re-energisation during the emergency shutdown state, directly implementing the energy isolation component of SYS-REQ-013. | 2026-03-22T16:10:03.243Z
STK-REQ-015 | SYS-REQ-015 | derives | EMC compliance is prerequisite for SIL 3 hardware certification | STK-REQ-015 requires operation within IEC 61000-4 series EMC limits. SYS-REQ-015 mandates hardware-independent safety-critical functions, which must be designed to IEC 61508 SIL 3 and therefore must meet the EMC requirements of IEC 61000-4 as part of the safety hardware certification. | 2026-03-22T16:09:49.987Z
STK-REQ-014 | SYS-REQ-011 | derives | Remote firmware update requires update event logging | STK-REQ-014 requires remote firmware update capability with rollback. SYS-REQ-011 defines the logging requirement that must capture firmware update events, and the remote monitoring interface (IFC-REQ-004) that supports the remote update pathway. The link is to the logging/monitoring system requirement that provides the update event audit trail. | 2026-03-22T16:09:49.365Z
STK-REQ-013 | SYS-REQ-015 | derives | Controls access requirements drive safety/process separation | STK-REQ-013 requires role-based controls access and audit trails. SYS-REQ-015 defines the safety-critical function independence which implements the separation of controls access levels the stakeholder requires: safety functions remain independent of the operator control software layer. | 2026-03-22T16:09:48.735Z
STK-REQ-012 | SYS-REQ-012 | derives | Energy reporting stakeholder need drives demand-response system requirement | STK-REQ-012 requires energy utilisation reports per zone and crop type. SYS-REQ-012 defines the demand-response capability that implements the energy monitoring and load management the stakeholder requires for these reports. | 2026-03-22T16:09:48.108Z
STK-REQ-004 | SYS-REQ-016 | derives | Zone isolation for maintenance derives from stakeholder maintenance need | STK-REQ-004 requires the system to allow zone maintenance without disrupting active crop cycles. SYS-REQ-016 defines the sanitisation sequence verification that must complete without affecting adjacent zones, directly addressing the stakeholder's need for isolated zone maintenance operations. | 2026-03-22T16:09:34.760Z
SYS-REQ-004 | IFC-REQ-005 | derives | CO2 bulk supply shutoff interface for safety interlock | SYS-REQ-004 requires CO2 interlock to shut off supply when concentration exceeds 5000 ppm. IFC-REQ-005 defines the CO2 Bulk Supply interface, including the hardwired shutoff mechanism that implements the SYS-REQ-004 interlock action. The interface specification is directly derived from the interlock requirement. | 2026-03-22T16:09:34.107Z
SYS-REQ-011 | IFC-REQ-004 | derives | Remote monitoring event forwarding interface | SYS-REQ-011 requires logging all environmental parameters and forwarding events to remote monitoring. IFC-REQ-004 defines the Cloud Monitoring Platform interface over which this remote event forwarding occurs. The interface exists because SYS-REQ-011 mandates remote notification capability. | 2026-03-22T16:09:33.452Z
SYS-REQ-012 | IFC-REQ-003 | derives | OpenADR demand-response input interface | SYS-REQ-012 requires response to OpenADR 2.0 demand-response events. IFC-REQ-003 defines the Energy Management/Smart Grid interface over which OpenADR signals are received. This is a direct derivation: the interface exists because the demand-response requirement mandates it. | 2026-03-22T16:09:22.698Z
SYS-REQ-005 | IFC-REQ-002 | derives | Crop recipe data from ERP drives lighting setpoints | SYS-REQ-005 requires LED lighting control within ±5% of crop recipe setpoints. IFC-REQ-002 defines the ERP interface that provides crop schedule and recipe data from which lighting setpoints are derived. | 2026-03-22T16:09:22.068Z
SYS-REQ-013 | IFC-REQ-001 | derives | Emergency shutdown trigger via BMS interface | SYS-REQ-013 requires emergency shutdown sequence execution within 30 seconds. IFC-REQ-001 defines the BMS interface that provides fire alarm and emergency stop inputs, which are the primary external triggers for initiating this sequence. | 2026-03-22T16:09:21.391Z
SYS-REQ-015 | SUB-REQ-011 | derives | Proof test interval maintains SIL 3 PFD over operational lifetime | SYS-REQ-015 requires SIL 3 achievement for safety functions. IEC 61511 makes proof testing a mandatory lifecycle requirement for SIL 3 systems — PFD targets cannot be maintained without periodic testing. SUB-REQ-011 specifies the test interval and coverage derived from the required PFD target. | 2026-03-22T15:41:59.129Z
SYS-REQ-009 | SUB-REQ-005 | derives | LED thermal interlock derives from SYS thermal protection requirement | SYS-REQ-009 specifies LED thermal trip at 85°C within 10s. SUB-REQ-005 incorporates this threshold. This is a genuine derivation: the specific temperature and response time from SYS-REQ-009 directly appear in SUB-REQ-005 without modification. | 2026-03-22T15:41:01.514Z
SYS-REQ-007 | SUB-REQ-005 | derives | pH dosing excess interlock derives from SYS dosing protection requirement | SYS-REQ-007 specifies pH dosing excess as a trip condition with 5s response. SUB-REQ-005 incorporates this as one of the threshold/response-time pairs evaluated by the Voted Logic Engine. | 2026-03-22T15:41:00.878Z
IFC-REQ-008 | VER-REQ-003 | verifies | End-to-end test covers LOTO inhibit verification | VER-REQ-003 includes emergency-stop testing which exercises the LOTO inhibit path at the Safety PLC level, partially verifying IFC-REQ-008 in the integration context. | 2026-03-22T15:41:00.228Z
SYS-REQ-015 | IFC-REQ-008 | derives | LOTO-to-PLC interface derives from safety independence mandate | SYS-REQ-015 requires safety functions to operate independently from process control. IFC-REQ-008 defines the hardwired LOTO inhibit interface that ensures maintenance lockout is enforced at the safety layer, not relying on process software. | 2026-03-22T15:40:59.601Z
SYS-REQ-011 | SUB-REQ-010 | derives | Interlock audit log derives from system-level data logging requirement | SYS-REQ-011 mandates logging of all environmental parameters and events. SUB-REQ-010 specifically covers the interlock event log, which is a safety-critical subset of the system-level logging requirement with additional non-volatile storage and capacity requirements driven by the safety audit trail need. | 2026-03-22T15:40:20.053Z
SUB-REQ-001 | VER-REQ-004 | verifies | Calibration test for CO2 sensor accuracy specification | Directly verifies the ±50 ppm accuracy requirement at multiple concentration points including the 5000 ppm trip threshold, using calibrated reference gas. | 2026-03-22T15:40:07.444Z
SUB-REQ-005 | VER-REQ-003 | verifies | End-to-end integration test for interlock response times | Functional test of the complete interlock chain from sensor exceedance to final element actuation. The measured response times directly verify the thresholds in SUB-REQ-005 under representative operating conditions. | 2026-03-22T15:40:06.128Z
IFC-REQ-007 | VER-REQ-002 | verifies | Integration test for Safety PLC to Trip Bus relay interface | The test directly exercises the energize-to-hold relay topology and wire-break detection required by IFC-REQ-007. Physical actuation of final elements verifies the complete signal path from PLC output card through relay module to final element. | 2026-03-22T15:38:49.906Z
IFC-REQ-006 | VER-REQ-001 | verifies | Integration test for CO2 sensor-to-PLC interface | The test injects known CO2 concentrations and simulates wire-break faults to verify both the functional accuracy and the fail-safe detection capability of the 4-20mA interface defined in IFC-REQ-006. PASS/FAIL criteria are directly derived from the ±50 ppm accuracy and fault detection requirements. | 2026-03-22T15:38:48.543Z
SYS-REQ-015 | SUB-REQ-009 | derives | Data diode/firewall implements network-level safety independence | SYS-REQ-015 requires the safety controller to be isolated from the process control network via a certified data diode or firewall. SUB-REQ-009 specifies this isolation device, directly implementing the network-level independence mandated by SYS-REQ-015. | 2026-03-22T15:38:01.473Z
SYS-REQ-015 | SUB-REQ-007 | derives | Hardwired trip bus enforces physical independence from process software | SYS-REQ-015 mandates safety-critical functions independent of process control software. SUB-REQ-007 specifies the hardwired trip bus architecture that physically enforces this independence for final element actuation, preventing process software from inadvertently commanding actuators. | 2026-03-22T15:38:00.713Z
SYS-REQ-004 | SUB-REQ-006 | derives | Safe state definition derives from CO2 interlock action specification | SYS-REQ-004 specifies the interlock action (shut off CO2, activate ventilation). SUB-REQ-006 formalises the complete safe state for all final elements and the manual reset requirement. | 2026-03-22T15:38:00.041Z
SYS-REQ-013 | SUB-REQ-005 | derives | Voted Logic Engine trip conditions derive from emergency shutdown SYS req | SYS-REQ-013 defines the emergency shutdown trigger conditions and response times; SUB-REQ-005 implements these as specific threshold checks within the Voted Logic Engine. | 2026-03-22T15:37:59.374Z
SYS-REQ-015 | SUB-REQ-004 | derives | SIL 3 scan time and watchdog requirements | SYS-REQ-015 mandates SIL 3 safety functions with independence from process network. SUB-REQ-004 specifies the Safety PLC 50ms scan time and hardware watchdog — requirements derived directly from IEC 61508 SIL 3 diagnostic coverage targets, which require scan completion within a defined diagnostic test interval. | 2026-03-22T15:37:58.739Z
SYS-REQ-015 | SUB-REQ-003 | derives | SIL 3 hardware certification prerequisite for safety layer | SYS-REQ-015 mandates SIL 3 for all safety-critical functions. SUB-REQ-003 specifies SIL 3 certification for the Safety PLC hardware. This is a genuine cascade: without a certified SIL 3 PLC, no software function in the safety layer can claim SIL 3 integrity. Hardware certification is the prerequisite. | 2026-03-22T15:37:45.444Z
SYS-REQ-004 | SUB-REQ-002 | derives | 2oo3 voting architecture derives from CO2 SIL 3 requirement | SYS-REQ-004 mandates SIL 3 CO2 interlock; achieving SIL 3 PFD requires voted redundancy. SUB-REQ-002 specifies the 2oo3 topology that satisfies the SIL 3 PFD target for this sensor function. | 2026-03-22T15:37:44.675Z
SYS-REQ-004 | SUB-REQ-001 | derives | CO2 independent sensor requirement from CO2 interlock SYS req | SYS-REQ-004 specifies 'independent safety-rated CO2 sensor' — SUB-REQ-001 defines the specific sensor accuracy, technology, and SIL rating that fulfils this independence mandate. | 2026-03-22T15:37:43.825Z
STK-REQ-010 | SYS-REQ-011 | derives | HACCP deviation reports require comprehensive environmental logging | HACCP reports identifying threshold exceedances can only be generated from underlying continuous environmental data records — logging is the prerequisite data source | 2026-03-22T15:05:59.457Z
STK-REQ-016 | SYS-REQ-015 | derives | Network resilience requires hardware-independent safety | 72-hour autonomous operation during network loss is only safe if safety-critical functions do not depend on the software controller or network connectivity — hardware independence is the implementation | 2026-03-22T15:05:58.777Z
STK-REQ-008 | SYS-REQ-016 | derives | Harvest crew safety extends to post-sanitation verification | Worker-comfort mode transitions must include sanitation sequence verification to prevent chemical residue exposure when crew re-enters for next crop setup | 2026-03-22T15:05:58.124Z
STK-REQ-006 | SYS-REQ-013 | derives | Maintenance lockout requirement extends to emergency reset | Lockout/tagout capability for maintenance is complementary to two-person emergency reset — both prevent actuator activation when personnel are in zone | 2026-03-22T15:05:57.504Z
STK-REQ-011 | SYS-REQ-012 | derives | Utility DR signals drive load curtailment requirement | STK specifies OpenADR 2.0 response within 5 minutes with crop-safe limits; SYS quantifies the 30% curtailment target and 4°C temperature relaxation envelope | 2026-03-22T15:05:38.335Z
STK-REQ-009 | SYS-REQ-011 | derives | Audit-ready logging requires comprehensive data recording | 2-year tamper-evident log retention for auditors requires 1-minute resolution recording with cryptographic integrity — the system logging requirement implements this capability | 2026-03-22T15:05:37.669Z
STK-REQ-005 | SYS-REQ-006 | derives | Sensor calibration supports nutrient control accuracy | pH/EC control within ±0.2/±0.1 tolerance is only achievable if sensors are regularly calibrated. Calibration routines are the maintenance interface to achieve nutrient control precision | 2026-03-22T15:05:36.999Z
STK-REQ-007 | SYS-REQ-003 | derives | Worker CO2 safety requires software concentration ceiling | 3000ppm software ceiling provides primary defence layer for worker safety; hardware interlock at 5000ppm is backup. Both required for SIL 3 per defence-in-depth | 2026-03-22T15:05:36.281Z
STK-REQ-007 | SYS-REQ-004 | derives | Worker CO2 safety requires hardware interlock | Harvest crew cannot monitor CO2 — hardware interlock at 5000ppm is the safety barrier protecting non-technical workers from asphyxiation per H-001 | 2026-03-22T15:05:35.681Z
STK-REQ-003 | SYS-REQ-008 | derives | HVAC failure response enables yield impact estimation | Facility manager needs yield impact data within 10 minutes of excursion; automatic LED reduction and adjacent zone compensation define the degraded envelope that the yield model calculates against | 2026-03-22T15:05:35.011Z
STK-REQ-002 | SYS-REQ-005 | derives | Recipe PAR adjustment requires lighting control precision | Grower technician adjusts PAR from HMI; system must achieve the specified intensity within tolerance for the adjustment to be meaningful | 2026-03-22T15:05:34.404Z
STK-REQ-001 | SYS-REQ-001 | derives | Zone dashboard accuracy requires precise temperature control | Dashboard displaying temperature is meaningless without tight control loop — grower relies on displayed values matching reality | 2026-03-22T15:05:33.793Z

## Linksets
Source Document | Target Document | Default Link Type | Link Count
subsystem-requirements | architecture-decisions |  | 0
system-requirements | architecture-decisions |  | 11
subsystem-requirements | verification-requirements |  | 54
interface-requirements | verification-requirements |  | 33
system-requirements | verification-requirements |  | 5
system-requirements | subsystem-requirements |  | 100
system-requirements | interface-requirements |  | 27
stakeholder-requirements | system-requirements |  | 25

## Sections
Document | Section | Short Code | Order | Requirements
architecture-decisions | Architecture Decisions | ARC | 0 | 11
interface-requirements | Interface Requirements | IFC | 0 | 42
stakeholder-requirements | Stakeholder Requirements | STK | 0 | 16
subsystem-requirements | Subsystem Requirements | SUB | 0 | 95
system-requirements | System Requirements | SYS | 0 | 20
verification-requirements | Verification Requirements | VER | 0 | 62